## Prescriptive Compliance Items
Commercial Prescriptive Measures Checklist | [7 empty] | 2020 City of Boulder Energy Conservation Code
Applies to: New Buildings and Additions with a construction valuation of <$500,000 and Level 1 & 2 Alterations
Project Address: | [7 empty] | Date:
DIRECTIONS: Compliance with these measures is required if the project uses the Prescriptive Compliance Path. Please complete this checklist and include it on an "Energy Conservation Code" sheet within the plans being submitted for permit application. Projects complying prescriptively also must meet Mandatory Measures and should include the Mandatory Measures Checklist as well.
Code Section | Focus Area | Code Description |  |  |  | Plan Drawing or Reference # to demonstrate compliance (N/A if not applicable) | Submitter Notes (e.g. If "N/A" Please explain why requirement does not apply or is not demonstrated on plans/specs) |  | Plans Examiner Notes (in office use)
BUILDING ENVELOPE
|  |  |  | All Other | Group R (Mixed Use)
TABLE C402.1.3 | Insulation | Roof | Insulation entirely above deck | Min R-33 continuous | Min R-33 continuous
|  |  | Metal buildings (w/R-5 thermal blocks) | Min R-19 + R-11 linear system | Min R-19 + R-11 linear system
|  |  | Attic and other | Min R-553 | Min R-53
|  | Walls, Above Grade | Mass | Min R-13.3 continuous | Min R-13.3 continuous
|  |  | Metal building | Min R-13 + R-19.5 continuous | Min R-13 + R-13 continuous
|  |  | Metal framed | Min R-13 + R-11 continuous | Min R-13 + R-11 continuous
|  |  | Wood framed and other | Min R-13 + R-9 continuous or R-19 + R5 continuous | Min R-13 + R-9 continuous or R-19 + R5 continuous
|  | Walls, Below Grade | Below-grade wall | Min R-7.5 continuous | Min R-10 continuous
|  | Floors | Mass | Min R-15 continuous | Min R-16.7 continuous
|  |  | Joist/framing | Min R-30 | Min R-30
|  | Slab-on-Grade Floors | Unheated slabs | Min R-15 for 24″ below | Min R-15 for 24″ below
|  |  | Heated slabs | Min R-20 for 48" below | Min R-20 for 48" below
|  | Opaque Doors | Swinging | Max U-0.37 | Max U-0.37
|  |  | Roll-up or sliding | Min R-4.75 | Min R-4.75
C402.2.6 |  | Radiant Heating | Radiant Panels, associated U-bends, and headers | Min R-3.5
C402.4.1 | Fenestration | Vertical fenestration | Area | Not to exceed 30% gross above-grade wall area
C402.4 |  |  | U-factor | Fixed | Max U-0.36
|  |  |  | Operable | Max U-0.45
|  |  |  | Entrance doors >50% glass area | Max U-0.63
|  |  | SHGC | Max N 0.51-0.61 / SEW 0.38-0.61
|  | Skylights | U-factor | Max U-0.50
|  |  | SHGC | Max 0.40
|  |  | Area | Not to exceed 3% gross floor area
|  |  | Curb Insulation | Skylight curbs shall be insulated to the level of roofs with insulation entirely above deck or R-5, whichever is less.
C402.4.2 |  | Minimum Skylight Fenestration | For enclosed spaces greater than 2,500 square feet, directly under a roof with ceiling heights greater than 15 feet, plan submitter must include supporting documentation showing the total daylight zone under skylights shall be not less than half the floor area and shall provide a minimum skylight area to daylight zone under skylights of either: 1. Not less than 3 percent with a skylight VT of at least 0.40; or 2. Provide a minimum skylight effective aperture of at least 1 percent or 3. Provide exception documentation.
C402.4.2.2 |  | Haze factor | Skylights in office, storage, automotive service, manufacturing, nonrefrigerated warehouse, retail store and distribution/sorting area spaces shall have a glazing material or diffuser with a haze factor greater than 90 percent when tested in accordance with ASTM D1003.
C402.5.3 |  | Rooms containing fuel-burning appliances | Where combustion air is supplied through openings in an exterior wall to a room or space containing a space-conditioning fuel-burning appliance, one of the following shall apply: 1. The room or space containing the appliance shall be located outside of the building thermal envelope. 2. The room or space containing the appliance shall be enclosed and isolated from conditioned spaces inside the building thermal envelope.
HEATING, VENTILATING, AND AIR CONDITIONING
C403.5 | Economizer | An air or water economizer shall be provided for the following cooling systems: 1. Chilled water systems with a total cooling capacity, less cooling capacity provided with air economizers Water-cooled Chilled-water Systems 1,320,000 Btu/h or Air-cooled Chilled-water Systems 1,720,000 Btu/h. 2. Individual fan systems with cooling capacity greater than or equal to 54,000 Btu/h (15.8 kW) in buildings having other than a Group R occupancy The economizer controls and
C403.5.1 | Integrated economizer control |  | Economizer systems shall be integrated with the mechanical cooling system and be configured to provide partial cooling even where additional mechanical cooling is required to provide the remainder of the cooling load.
C403.5.2 | Economizer heating system impact |  | HVAC system design and economizer controls shall be such that economizer operation does not increase building heating energy use during normal operation.
C403.5.3 | Air economizers | Design capacity | Air economizer systems shall be configured to modulate outdoor air and return air dampers to provide up to 100 percent of the design supply air quantity as outdoor air for cooling
|  | Control signal | Economizer controls and dampers shall be configured to sequence the dampers with the mechanical cooling equipment and shall not be controlled by only mixed-air temperature
|  | High-limit shutoff | Air economizers shall be configured to automatically reduce outdoor air intake to the design minimum outdoor air quantity when outdoor air intake will not reduce cooling energy usage.
|  | Relief of excess outdoor air system | Systems shall be capable of relieving excess outdoor air during air economizer operation to prevent over pressurizing the building. The relief air outlet shall be located to avoid recirculation into the building.
C403.5.4 | Water-side economizers | Design capacity | Water economizer systems shall be configured to cool supply air by indirect evaporation and providing up to 100 percent of the expected system cooling load at outdoor air temperatures of not greater than 50°F (10°C) dry bulb/45°F (7°C) wet bulb.
|  | Maximum pressure drop | Precooling coils and water-to-water heat exchangers used as part of a water economizer system shall either have a waterside pressure drop of less than 15 feet (45 kPa) of water or a secondary loop shall be created so that the coil or heat exchanger pressure drop is not seen by the circulating pumps when the system is in the normal cooling (noneconomizer) mode.
INTERIOR LIGHTING
C405.3 | Interior lighting power requirements |  | A building complies with this section when its total connected interior lighting power calculated under Section C405.3.1 is not greater than the interior lighting power allowance calculated under Section C405.3.2. Indicate if Building Area Method or Space-by-Space Method is used to determine Lighting Power Allowance and included project specific lighting calculations demonstrating compliance on the Lighting Calculations Tab. Alternatively, COMCheeck can be used to demonstrate compliance. Note: select the Boulder 2020 Code on the Project Tab.

## Lighting Calculations
Space-by-Space Method Directions: 1. List all unique space types per the 2020 City of Boulder Energy Conservation Code Table C405.3.2(2). 2. Identify space type from the drop down menu. 3. Indicate space square footage. 4. List all proposed lighting fixtures including existing-to-remain fixtures. 4. Identify fumber of fixtures per space. 5. For watts per fixture enter the luminaire wattage for installed lamp and ballast using manufacturer's data.
ROOM Number | COBECC Space Type | Space SQ FT | COBECC LPD (w/SF) | Allowable Watts | Fixture Type | Number of Fixtures | Watts per Fixture | Designed Watts | Designed LPD (w/SF)
(add rows as needed)
Total Designed Watts must be less than Total Allowable Watts |  |  |  | 0 |  |  |  | 0
Building Area Method Directions: 1. List building levels and sqare footages. 2. Identify COBECC LPD based on the 2020 City of Boulder Energy Conservation Code Table C405.3.2(1). 3. List all proposed lighting fixtures including existing-to-remain fixtures. 4. Identify fumber of fixtures per space. 5. For watts per fixture enter the luminaire wattage for installed lamp and ballast using manufacturer's data.
Building Level | SQ FT | COBECC LPD (w/SF) | Allowable Watts | Fixture Type | Number of Fixtures | Watts per Fixture | Designed Watts
(add rows as needed)
Total Designed Watts must be less than Total Allowable Watts |  |  | 0 |  |  |  | 0