## Mandatory Compliance Items
Commercial Mandatory Measures Checklist |  |  |  | 2020 City of Boulder Energy Conservation Code
Applies to: All New Buildings, Additions, Alterations and Repairs which require a permit from the City.
Project Address: |  |  |  | Date:
DIRECTIONS: Compliance with these Mandatory Measures is required whether the project is demonstrating compliance through the Performance or Prescriptive Path. Please complete this checklist and include it on an "Energy Conservation Code" sheet within the plans being submitted for permit application.
Code Section | Focus Area | Code Description | Plan Drawing or Reference # to demonstrate compliance (N/A if not applicable) | Submitter Notes (e.g. If "N/A" Please explain why requirement does not apply or is not demonstrated on plans/specs) | Plans Examiner Notes (in office use)
C401.2 | Check compliance path applicable | New Construction < $500,000 |  |  | Mandatory and Prescriptive Compliance
|  | New Construction >/= $500,000 |  |  | Mandatory and Performance Modeling
|  | Addition > 1,000sf |  |  | Mandatory and Performance Modeling
|  | Addition < 1,000sf |  |  | Mandatory and Prescriptive Compliance
|  | Alteration Level 1 |  |  | Mandatory and Prescriptive Compliance
|  | Alteration Level 2 |  |  | Mandatory and Prescriptive Compliance
|  | Alteration Level 3 |  |  | Mandatory and Performance Modeling
|  | Alteration Level 4 |  |  | Mandatory and Performance Modeling
ADMINISTRATIVE
C103.2 | Construction documents shall clearly indicate the location, nature and extent of the work proposed, and show in detail pertinent data and features of the building, systems and equipment. | 1. Insulation materials and their R-values.
2. Fenestration U-factors and solar heat gain coefficients
3. Area-weighted U-factor and solar heat gain coefficient (SHGC) calculations.
4. Mechanical system design criteria.
5. Mechanical and service water heating systems and equipment types, sizes and efficiencies.
6. Economizer description.
7. Equipment and system controls.
8. Fan motor horsepower (hp) and controls.
9. Duct sealing, duct and pipe insulation and location.
10. Lighting fixture schedule with wattage and control narratives.
11. Location of daylight zones on floor plans.
12. Air sealing details.
C103.2.1 | Building thermal envelope depiction | The building thermal envelope shall be represented on the construction drawings.
C303.1.3 | Fenestration and Doors | U-factors of fenestration products shall be determined for windows, doors and skylights, U-factor ratings in accordance with NFRC 100. Drawings shall indicate NRFC labels or certicates must be provided to the building official prior to Certificate of Occupancy in compliance with NFRC 100. |  |  | Building Condition: NFRC Label Certificate
BUILDING ENVELOPE
C402.5.1 | Air Barriers | The entire building envelope shall be designed and constructed with a continuous air barrier.
C402.5.1.1 | Air Barrier Design/ Construction | The air barrier shall be designed and noted in an approved manner per the specified code - joints, seams, penetrations, and recessed light fixtures sealed
C402.5.1.2 | Building Test | The completed building shall be tested and the air leakage rate of the building envelope shall not exceed 0.40 cfm/ft2 at a pressure differential of 0.3 inches water gauge (2.0 L/s • m2 at 75 Pa) in accordance with ASTM E 779 or an equivalent method approved by the code official. |  |  | Building Condition: Commercial Air Leakage Testing
C402.5.1.3 | Dwelling Unit Air Infiltration | A sampling of dwelling units shall be tested and results shall not exceed 0.25cfm/ft2. See code for more details. |  |  | Building Condition: Commercial Air Leakage Testing
C402.5.2 | Fenestration | Factory-built fenestration and doors are labeled as meeting air leakage requirements
C402.4.6 | Air intakes, exhaust openings, stairways and shafts. | Stairway enclosures, elevator shaft vents and other outdoor air intakes and exhaust openings integral to the building envelope shall be provided with dampers in accordance with Section C403.7.7.
C402.5.6 | Loading Dock Weather seals | Cargo doors and loading dock doors are equipped with weather seals to restrict infiltration when vehicles are parked in the doorway.
C402.5.7 | Vestibules | Building entrances shall be protected with an enclosed vestibule, with all doors opening into and out of the vestibule equipped with self-closing devices
C402.5.8 | Recessed lighting | Recessed luminaires installed in the building thermal envelope shall be IC-rated and labeled as having an air leakage rate of not more 2.0 cfm
HEATING, VENTILATING, AND AIR CONDITIONING
C403.2.1 | Zone isolation required | HVAC systems serving zones that are over 25,000 square feet in floor area or that span more than one floor and are designed to operate or be occupied nonsimultaneously shall be divided into isolation areas.
C403.2.2 | Ventilation | Ventilation, either natural or mechanical, shall be provided in accordance with Chapter 4 of the International Mechanical Codes.
C403.3 | Heating and cooling equipment efficiencies | Heating and cooling equipment installed in mechanical systems shall be sized in accordance with Section C403.3.1
C403.3.1 | Equipment sizing | The output capacity of heating and cooling equipment shall be not greater than that of the smallest available equipment size that exceeds the loads calculated in accordance with Section C403.1.1.
C403.3.2 | HVAC equipment performance requirements | Equipment shall meet the minimum efficiency requirements of Tables C403.3.2(1) through C403.3.2(9) when tested and rated in accordance with the applicable test procedure.
C403.3.2.1 | Water-cooled centrifugal chilling packages | Equipment not designed for operation at AHRI Standard 550/590 test conditions of 44°F leaving chilled-water temperature and 2.4 gpm/ton evaporator fluid flow and 85°F entering condenser water temperature with 3 gpm/ton condenser water flow shall have maximum fullload kW/ton and part-load ratings as identified in Section C403.3.2.1
C403.3.2.2 | Positive displacement (air- and watercooled) chilling packages | Equipment with a leaving fluid temperature higher than 32°F and water-cooled positive displacement chilling packages with a condenser leaving fluid temperature below 115°F shall meet the requirements of Table C403.3.2(7)
C403.4.1 | Thermostatic controls | The supply of heating and cooling energy to each zone shall be controlled by individual thermostatic controls capable of responding to temperature within the zone.
C403.4.1.1 | Heat pump supplementary heat | Heat pumps having supplementary electric resistance heat shall have controls that, except during defrost, prevent supplementary heat operation where the heat pump can provide the heating load
C403.4.1.2 | Deadband | Where used to control both heating and cooling, zone thermostatic controls shall be configured to provide a temperature range or deadband of not less than 5°F within which the supply of heating and cooling energy to the zone is shut off or reduced to a minimum.
C403.4.1.3 | Setpoint overlap restriction | Where a zone has a separate heating and a separate cooling control located within the zone, a limit switch, mechanical stop or direct digital control system with software programming shall be configured to prevent the heating setpoint from exceeding the cooling setpoint and to maintain a deadband in accordance with Section C403.4.1.2.
C403.4.1.4 | Heated or cooled vestibules | The heating system for heated vestibules and air curtains with integral heating shall be provided with controls configured to shut off the source of heating when the outdoor air temperature is greater than 45°F
C403.4.1.5 | Hot water boiler outdoor temperature setback control | Hot water boilers that supply heat to the building through one- or two-pipe heating systems shall have an outdoor setback control that lowers the boiler water temperature based on the outdoor temperature
C403.4.1.6 | Mechanical system shutoff | Operable wall or roof openings, overhead doors, cargo doors, sliding doors, folding and accordion-style wall systems, and other loading dock-style doors that open to the outdoors shall be equipped with interlock controls that disable the heating, cooling and humidity control equipment that serves the area or zone adjacent to the opening.
C403.4.2 | Off-hour controls | Each zone shall be provided with thermostatic setback controls that are controlled by either an automatic time clock or programmable control system.
C403.4.2.1 | Thermostatic setback | Thermostatic setback controls shall be configured to set back or temporarily operate the system to maintain zone temperatures down to 55°F (13°C) or up to 85°F
C403.4.2.2 | Automatic setback and shutdown | Automatic time clock or programmable controls shall be capable of starting and stopping the system for seven different daily schedules per week and retaining their programming and time setting during a loss of power for not fewer than 10 hours.
C403.4.2.3 | Automatic start | Automatic start controls shall be provided for each HVAC system.
C403.5.5 | Economizer fault detection and diagnostics | Air-cooled unitary direct-expansion units listed in Tables C403.3.2(1) through C403.3.2(3) and variable refrigerant flow (VRF) units that are equipped with an economizer shall include a fault detection and diagnostics
C403.7.1 | Demand control ventilation | Demand control ventilation shall be provided for spaces larger than 500 square feet and with an average occupant load of 25 people or greater per 1,000 square feet of floor area
C403.7.2 | Enclosed parking garage ventilation controls | Enclosed parking garages shall employ contamination-sensing devices and automatic controls configured to stage fans or modulate fan average airflow rates to 50 percent or less of design capacity, or intermittently operate fans less than 20 percent of the occupied time or as required to maintain acceptable contaminant levels
C403.7.3 | Ventilation air heating control | Units that provide ventilation air to multiple zones and operate in conjunction with zone heating and cooling systems shall not use heating or heat recovery to warm supply air to a temperature greater than 60°F (16°C) when representative building loads or outdoor air temperatures indicate that the majority of zones require cooling.
C403.7.4 | Energy recovery ventilation systems | Where the supply airflow rate of a fan system exceeds the values specified in Table C403.7.4, the system shall include an energy recovery system.
C403.7.5 | Kitchen exhaust systems | Replacement air introduced directly into the exhaust hood cavity shall not be greater than 10 percent of the hood exhaust airflow rate
C403.7.6 | Automatic control of HVAC systems serving guestrooms | In Group R-1 buildings containing more than 50 guestrooms, each guestroom shall be provided with controls complying with the provisions of this Section
C403.7.7 | Shutoff dampers | Outdoor air intake and exhaust openings and stairway and shaft vents shall be provided with Class I motorized dampers
C403.8.1 | Allowable fan horsepower | Each HVAC system having a total fan system motor nameplate horsepower exceeding 5 hp (3.7 kW) at fan system design conditions shall not exceed the allowable fan system motor nameplate hp (Option 1) or fan system bhp (Option 2) shown in Table C403.8.1(1)
C403.8.2 | Motor nameplate horsepower | For each fan, the fan brake horsepower shall be indicated on the construction documents and the selected motor shall be not larger than the first available motor size greater than this Section allows.
C403.8.3 | Fan efficiency | Fans shall have a fan efficiency grade (FEG) of not less than 67, as determined in accordance with AMCA 205 by an approved, independent testing laboratory and labeled by the manufacturer.
C403.8.4 | Fractional hp fan motors | Motors for fans that are not less than 1 /12 hp (0.062 kW) and less than 1 hp (0.746 kW) shall be electronically commutated motors or shall have a minimum motor efficiency of 70 percent
C403.10 | Walk-in coolers, walk-in freezers, refrigerated warehouse coolers and refrigerated warehouse freezers | Refrigerated warehouse coolers and refrigerated warehouse freezers shall comply with this Section
C403.11 | Construction of HVAC system elements | Ducts, plenums, piping and other elements that are part of an HVAC system shall be constructed and insulated in accordance with Sections C403.11.1 through C403.11.3.1.
C403.11.3 | Piping insulation | Piping serving as part of a heating or cooling system shall be thermally insulated in accordance with Table C403.11.3.
C403.12 | Mechanical systems located outside of the building thermal envelope | Mechanical systems providing heat outside of the thermal envelope of a building shall comply with Sections C403.12.1 through C403.12.3
SERVICE WATER HEATING
C404.3 | Heat Traps | Water heating equipment not supplied with integral heat traps and servicing noncirculating systems shall be provided with heat traps on supply and discharge pipingt associated with the equipment.
C404.4 | Piping Insulation | For automatic-circulating hot water and heat-traced systems, piping shall be insulated with not less than 1 inch of insulation having a conductivity not exceeding 0.27 Btu per inch/h × ft2 × °F. The first 8 feet of piping in non-hot-water-supply temperature maintenance systems served by equipment without integral heat traps shall be insulated with 0.5 inch of material having a conductivity not exceeding 0.27 Btu per inch/h × ft2 × °F.
C404.5 | Heated water supply piping | Heated water supply piping shall be in accordance with Section C404.5.1 or C404.5.2.
C404.6 | Heated-water circulating and temperature maintenance systems | Heated-water circulation systems shall be in accordance with Section C404.6.
C404.7 | Demand recirculation controls | Demand recirculation water systems shall have controls that comply with C404.7
C404.8 | Drain water heat recovery units | Drain water heat recovery units shall comply with CSA B55.2.
C404.9 | Energy consumption of pools and permanent spas | The energy consumption of pools and permanent spas shall comply with the requirements in Sections C404.9.1 through C404.9.3.
ELECTRICAL POWER & LIGHTING SYSTEMS
C405.1.1 | Lighting for dwelling units | Not less than 90 percent of the luminaires in dwelling units shall be provided by lamps with an efficacy of not less than 65 lm/W or shall be luminaires with an efficacy of not less than 45 lm/W.
C405.2.1 | Occupant sensor controls | Occupant sensor controls shall be installed to control lights in the following space types: 1. Classrooms/lecture/training rooms. 2. Conference/meeting/multipurpose rooms. 3. Copy/print rooms. 4. Lounges/breakrooms. 5. Enclosed offices. 6. Open plan office areas. 7. Restrooms. 8. Storage rooms. 9. Locker rooms. 10. Other spaces 300 square feet or less 11. Warehouse storage areas.
C405.2.2 | Time-switch controls | Each area of the building that is not provided with occupant sensor controls
C405.2.3 | Daylight-responsive controls | Daylight-responsive controls complying with Section C405.2.3.1 shall be provided to control the electric lights within daylight zones
C405.2.6 | Exterior lighting controls | Exterior lighting systems shall be provided with controls that comply with Sections C405.2.6.1 through C405.2.6.4.
C405.2.7 | Parking garage lighting control | Lighting for parking garages shall have controls that comply with C405.2.7
C405.5 | Exterior lighting power requirements | The total connected exterior lighting power calculated in accordance with Section C405.4.1 shall be not greater than the exterior lighting power allowance calculated in accordance with Section C405.5.2
C405.6 | Dwelling electrical meter | Each dwelling unit located in a Group R-2 building shall have a separate electrical meter.
C405.7 | Electrical transformers | Low-voltage dry-type distribution electric transformers shall meet the minimum efficiency requirements of Table C405.7
C405.11 | Electric vehicle (EV) charging for new construction | New building shall be provided with electric vehicle charging in accordance with this C405.11 and the National Electrical Code (NFPA 70).
SOLAR READY BUILDINGS
C406.2 | Solar Zone | All commercial buildings shall dedicate a solar zone, shown on the plans that has a minimum total area per C406.2. The solar zone shall be no less than 80 ft2 and no side shall be less than 5ft in length. The solar zone shall be oriented between 90 deg and 270 deg of true North on steep sloped roofs. No obstructions or shading from vents, architectural features, equipment, etc. shall be located in the solar zone.
C406.2.4 | Structural Design Loads | For areas of the roof designated as the solar zone, the structural design loads for the roof dead and live loads shall be clearly indicated on the construction documents. Collateral loads for future solar systems is not required.
C406.3 | Interconnection Pathways | The construction documents shall indicate a location for inverters and metering equipment and a pathway for routing of conduit from the solar zone to the point of interconnection of the electrical service.
C406.5 | Main Service Panel | The main electrical service panel shall have a minimum busbar rating of no less than 200 Amps and shall have a reserved space to allow for installation of double pane circuit breakers for a future solar electric installation.
SYSTEM COMMISSIONING
C408.1 | Mechanical System Commissioning and Completion Requirements | Prior to the final mechanical and plumbing inspections, the registered design professional or approved agency shall provide evidence of mechanical systems commissioning and completion in accordance with the provisions of this section. |  |  | Building Condition: Commissioning
C408.3.1 | Lighting System Functional Testing | Prior to passing final inspection, the registered design professional shall provide evidence that the lighting control systems have been tested to ensure that control hardware and software are calibrated, adjusted, programmed and in proper working condition in accordance with the construction documents and manufacturer’s instructions. |  |  | Building Condition: Commissioning