## Prescriptive Compliance Items
2024 Boulder Energy Code - Commercial Prescriptive Measures Checklist | [7 empty] | 2024 City of Boulder Energy Conservation Code
Applies to: New Buildings and Additions with a construction valuation of <$500,000 and Level 1 & 2 Alterations
Project Address: | [7 empty] | Date:
DIRECTIONS: Compliance with these measures is required if the project uses the Prescriptive Compliance Path. Please complete this checklist and include it on an "Energy Conservation Code" sheet within the plans being submitted for permit application. Projects complying prescriptively no longer have to submit a mandatory checklist as these measere are now contained within this document. Provide exception documentation, if applicable.
Commercial New Construction ---- Please fill out Table 1 and provide all requested supporting documentation.
Commercial Additions ------------- Please fill out Table 2 and provide all requested supporting documentation.
Commercial Alterations ----------- Please fill out Table 3 and provide all requested supporting documentation.
Project Summary/Details:
Table 1. New Construction Compliance
C401.2 New Construction | Compliance Path | Construction Valuation |  |  |  | Plan Drawing or Reference # to demonstrate compliance (N/A if not applicable) | Submitter Notes |  | Permit Reviewer Notes
|  | New Construction < $500,000 | [6 empty] | Prescriptive Compliance
|  | New Construction >/= $500,000 |  |  |  |  | IF selected, STOP and complete the PERFORMANCE CHECKLIST instead |  | Performance Compliance Only
Table 2. Additions Compliance
C401.3 Exisiting Buildings C502.1 Additions | Compliance Path | Construction Valuation |  |  |  | Plan Drawing or Reference # to demonstrate compliance (N/A if not applicable) | Submitter Notes |  | Permit Reviewer Notes
|  | Additions < $500,000 | [6 empty] | Prescriptive Compliance
|  | Additions >/= $500,000 |  |  |  |  | IF selected, STOP and complete the PERFORMANCE CHECKLIST instead |  | Performance Compliance Only
Table 3. Alterations Compliance
C401.3 Exisiting Buildings C503.1 Alterations | Compliance Path | Alteration Type |  |  |  | Plan Drawing or Reference # to demonstrate compliance (N/A if not applicable) | Submitter Notes |  | Permit Reviewer Notes
|  | Alteration Level 1 or Level 2 | [6 empty] | Prescriptive Compliance
|  | Alteration Level 3 |  |  |  |  | IF selected, STOP and complete the PERFORMANCE CHECKLIST instead |  | Performance Compliance Only
|  | Alteration Level 3 with substantial mechanical AND envelope alterations | [6 empty] | Performance Compliance Only
Code Section | Focus Area | Code Description |  |  |  | Plan Drawing or Reference # to demonstrate compliance (N/A if not applicable) | Submitter Notes (e.g. If "N/A" Please explain why requirement does not apply or is not demonstrated on plans/specs) |  | Plans Examiner Notes (in office use)
ADMINISTRATIVE
C103.2 | Construction documents shall clearly indicate the location, nature and extent of the work proposed, and show in detail pertinent data and features of the building, systems and equipment. | 1. Energy compliance path.
2. Insulation materials and their R-values.
3. Fenestration U-factors and solar heat gain coefficients (SHGCs).
4. Area-weighted U-factor and solar heat gain coefficient (SHGC) calculations.
5. Mechanical system design criteria.
6. Mechanical and service water heating systems and equipment types, sizes and efficiencies.
7. Economizer description.
8. Equipment and system controls.
9. Fan motor horsepower (hp) and controls.
10. Duct sealing, duct and pipe insulation and location.
11. Lighting fixture schedule with wattage and control narrative.
12. Location of daylight zones on floor plans.
13. Air barrier and air sealing details, including the location of the air barrier.
14. Details of additional electric infrastructure, including branch circuits, conduit, or pre-wiring, and panel capacity in compliance with the provisions of this code.
15. Location and size of the solar-ready zone.
16 Structural design loads of roof dead load and roof live load.
17. Pathways for routing of conduit from the solar-ready zone to the electrical service panel.
18. Number and location of EV capable light spaces.
19. Number and location of EV capable spaces.
20. Number and location of EV ready spaces.
21. Number and location of EVSE installed spaces.
22. Locations of conduit and termination points serving the aforementioned parking spaces.
23. Location for condensate drainage where combustion equipment for space heating and water heating is installed.
24. Additional Conservation measures selected for compliance with C406.
C103.2.1 | Building thermal envelope depiction | The building thermal envelope shall be represented on the construction drawings in both plan and trans-sectional views and shall outline the extent of the building thermal envelope.
C303.1.3 | Fenestration product rating | U-factors of fenestration products shall be determined as follows: 1. For windows, doors and skylights, U-factor ratings shall be determined in accordance with NFRC 100. 2. Where required for garage doors and rolling doors, U-factor ratings shall be determined in accordance with either NFRC 100 or ANSI/DASMA 105. | [6 empty] | Building Condition: NFRC Label Certificate
Code Section | Focus Area | Code Description |  |  |  | Plan Drawing or Reference # to demonstrate compliance (N/A if not applicable) | Submitter Notes (e.g. If "N/A" Please explain why requirement does not apply or is not demonstrated on plans/specs) |  | Plans Examiner Notes (in office use)
BUILDING ENVELOPE
|  |  |  | All Other | Group R (Mixed Use)
TABLE C402.1.3 and C402.1.4 | Insulation | Roof | Insulation entirely above deck | Minimum R-33 continuous
|  |  | Metal buildings | Min R-19 + R-11 linear system
|  |  | Attic and other | Min R-53
|  | Walls, Above Grade | Mass | Min R-13.3 continuous
|  |  | Metal building | Min R-13 + R-19.5 continuous | Min R-13 + R-13 continuous
|  |  | Metal framed | Min R-13 + R-11 continuous
|  |  | Wood framed and other | Min R-13 + R-9 continuous or R-19 + R5 continuous | [5 empty] | Table C402.1.3 | Table C402.1.4
|  | Walls, Below Grade | Below-grade wall | Min R-7.5 continuous | Min R-10 continuous
|  | Floors | Mass | Min R-15 continuous | Min R-16.7 continuous
|  |  | Joist/framing | Min R-30
|  | Slab-on-Grade Floors | Unheated slabs | Min R-15 for 24″ below
|  |  | Heated slabs | Min R-20 for 48" below + R-5 full slab
|  | Opaque Doors | Swinging | Max U-0.37
|  |  | Roll-up or sliding | Max U-0.31
C402.2.6 |  | Radiant Heating | Radiant Panels, associated U-bends, and headers | Min R-3.5
C402.4.1 | Fenestration | Vertical fenestration | Area | Not to exceed 30% gross above-grade wall area
C402.4 |  |  | U-factor | Fixed | Max U-0.36
|  |  |  | Operable | Max U-0.45
|  |  |  | Entrance doors >50% glass area | Max U-0.63
|  |  | SHGC | Projection Factor (PF) | Fixed ¦ Operable
|  |  |  | PF < 0.2 | 0.38 ¦ 0.33
|  |  |  | 0.2 ≤ PF < 0.5 | 0.46 ¦ 0.40
|  |  |  | PF ≥ 0.5 | 0.61 ¦ 0.53
|  | Skylights | U-factor | Max U-0.50
|  |  | SHGC | Max U-0.40
|  |  | Area | Not to exceed 3% gross floor area
|  |  | Curb Insulation | Skylight curbs shall be insulated to the level of roofs with insulation entirely above deck or R-5, whichever is less.
C402.4.2 |  | Minimum Skylight Fenestration | Skylights shall be provided in enclosed spaces greater than 2,500 square feet in floor area, directly under a roof with not less than 75 percent of the ceiling area with a ceiling height greater than 15 feet, and used as an office, lobby, atrium, concourse, corridor, storage space, gymnasium/exercise center, convention center, automotive service area, space where manufacturing occurs, nonrefrigerated warehouse, retail store, distribution/sorting area, transportation depot or workshop. Plan submitter must include supporting documentation showing the total daylight zone under skylights shall be not less than half the floor area and shall provide a minimum skylight area to daylight zone under skylights of either: 1. Not less than 3 percent where all skylights have a VT of not less than 0.40, or VTannual of not less than 0.26 as determined in accordance with Section C303.1.3; or 2. Provide a minimum skylight effective aperture, determined in accordance with Equation 4-3, of not less than 1 percent using a skylight's VT, or not less than 0.66 percent using a Tubular Daylighting VTannual rating. Provide exception documentation, if applicable.
C402.4.2.2 |  | Haze factor | Skylights in office, storage, automotive service, manufacturing, nonrefrigerated warehouse, retail store and distribution/sorting area spaces shall have a glazing material or diffuser with a haze factor greater than 90 percent when tested in accordance with ASTM D1003.
C402.5.1 | Air Leakage | Air Barriers | A continuous air barrier shall be provided throughout the building thermal envelope. The continuous air barrier shall be located on the inside or outside of the building thermal envelope, located within the assemblies composing the building thermal envelope, or any combination thereof.
C402.5.1.1 |  | Air barrier construction | The continuous air barrier shall be constructed to comply with the following: 1. The air barrier shall be continuous for all assemblies that are the thermal envelope of the building and across the joints and assemblies. 2. Air barrier joints and seams shall be sealed, including sealing transitions in places and changes in materials. The joints and seals shall be securely installed in or on the joint for its entire length so as not to dislodge, loosen or otherwise impair its ability to resist positive and negative pressure from wind, stack effect and mechanical ventilation. 3. Penetrations of the air barrier shall be caulked, gasketed or otherwise sealed in a manner compatible with the construction materials and location. Sealing shall allow for expansion, contraction and mechanical vibration. Joints and seams associated with penetrations shall be sealed in the same manner or taped. Sealing materials shall be securely installed around the penetration so as not to dislodge, loosen or otherwise impair the penetrations’ ability to resist positive and negative pressure from wind, stack effect and mechanical ventilation. Sealing of concealed fire sprinklers, where required, shall be in a manner that is recommended by the manufacturer. Caulking or other adhesive sealants shall not be used to fill voids between fire sprinkler cover plates and walls or ceilings. 4. Recessed lighting fixtures shall comply with Section C402.5.8. Where similar objects are installed that penetrate the air barrier, provisions shall be made to maintain the integrity of the air barrier.
C402.5.1.2 |  | Building thermal envelope testing | The building thermal envelope shall be tested in accordance with ASTM E779, ANSI/RESNET/ICC 380, ASTM E3158 or ASTM E1827 or an equivalent method approved by the code official. The measured air leakage shall not exceed 0.25 cfm/ft2 of the building thermal envelope area at a pressure differential of 0.3 inch water gauge (75 Pa). Alternatively, portions of the building shall be tested and the measured air leakages shall be area weighted by the surface areas of the building thermal envelope in each portion. The weighted-average test results shall not exceed the whole building leakage limit. | [5 empty] | Building Condition: Commercial Air Leakage Testing
C402.5.1.4 |  | Dwelling and sleeping unit enclosure testing | The dwelling or sleeping unit envelope shall be tested in accordance with ASTM E779, ANSI/RESNET/ICC 380, ASTM E1827 or an equivalent method approved by the code official. The measured air leakage shall not exceed 0.20 cfm/ft2 (1.02 L/s • m2) of the testing unit enclosure area at a pressure differential of 0.2 inch water gauge (50Pa). Where multiple dwelling units or sleeping units or other occupiable conditioned spaces are contained within one building thermal envelope, each unit shall be considered an individual testing unit, and the building air leakage shall be the weighted average of all testing unit results, weighted by each unit’s enclosure area. | [5 empty] | Building Condition: Multifamily Air Leakage Testing
C402.5.2 |  | Air leakage of fenestration | The air leakage of fenestration assemblies shall meet the provisions of Table C402.5.2. | [6 empty] | Table C402.5.2
C402.5.3 |  | Rooms containing fuel-burning appliances | Where combustion air is supplied through openings in an exterior wall to a room or space containing a space-conditioning fuel-burning appliance, one of the following shall apply: 1. The room or space containing the appliance shall be located outside of the building thermal envelope. 2. The room or space containing the appliance shall be enclosed and isolated from conditioned spaces inside the building thermal envelope. 3. Provide exception documentation, if applicable.
C402.4.6 |  | Air intakes, exhaust openings, stairways and shafts. | Stairway enclosures, elevator shaft vents and other outdoor air intakes and exhaust openings integral to the building envelope shall be provided with dampers in accordance with Section C403.7.7.
C402.5.6 |  | Loading dock weather seals | Cargo door openings and loading door openings shall be equipped with weather seals that restrict infiltration and provide direct contact along the top and sides of vehicles that are parked in the doorway.
C402.5.7 |  | Vestibules | Building entrances shall be protected with an enclosed vestibule, with all doors opening into and out of the vestibule equipped with self-closing devices.
C402.5.8 |  | Recessed lighting | Recessed luminaires installed in the building thermal envelope shall be all of the following: 1. IC-rated. 2. Labeled as having an air leakage rate of not more 2.0 cfm (0.944 L/s) when tested in accordance with ASTM E283 at a 1.57 psf (75 Pa) pressure differential. 3. Sealed with a gasket or caulk between the housing and interior wall or ceiling covering.
C402.5.9 |  | Operable openings interlocking | Where occupancies utilize operable openings to the outdoors that are larger than 40 square feet in area, such openings shall be interlocked with the heating and cooling system so as to raise the cooling setpoint to 90°F and lower the heating setpoint to 55°F whenever the operable opening is open. The change in heating and cooling setpoints shall occur within 10 minutes of opening the operable opening.
HEATING, VENTILATING, AND AIR CONDITIONING
C403.2.1 |  | Zone isolation required | HVAC systems serving zones that are over 25,000 square feet in floor area or that span more than one floor and are designed to operate or be occupied nonsimultaneously shall be divided into isolation areas.
C403.2.2 |  | Ventilation | Ventilation, either natural or mechanical, shall be provided in accordance with Chapter 4 of the International Mechanical Code.
C403.3 |  | Heating and cooling equipment efficiencies | Heating and cooling equipment installed in mechanical systems shall be sized in accordance with Section C403.3.1
C403.2.3 |  | Fault detection and diagnostics | New buildings with an HVAC system serving a gross conditioned floor area of 25,000 square feet (2,322.5 m2) or larger shall include a fault detection and diagnostics (FDD) system to monitor the HVAC system's performance and automatically identify faults.
C403.3 |  | Mechanical system energy source | All mechanical systems such as for heating, cooling, water heating, clothes drying and cooking shall be all-electric or fueled by other non-fossil fuel derived energy source.
C403.3.2 |  | Equipment sizing | The output capacity of heating and cooling equipment shall be not greater than that of the smallest available equipment size that exceeds the loads calculated in accordance with Section C403.1.1.
C403.3.3 |  | HVAC equipment performance requirements | Equipment shall meet the minimum efficiency requirements of Tables C403.3.2(1) through C403.3.2(16) when tested and rated in accordance with the applicable test procedure. | [6 empty] | Table C403.3.2(1) | Table C403.3.2(2) | Table C403.3.2(3) | Table C403.3.2(4) | Table C403.3.2(5) | Table C403.3.2(6) | Table C403.3.2(7) | Table C403.3.2(8) | Table C403.3.2(9) | Table C403.3.2(10) | Table C403.3.2(11) | Table C403.3.2(12) | Table C403.3.2(13) | Table C403.3.2(14) | Table C403.3.2(15) | Table C403.3.2(16)
C403.3.2.1 |  | Water-cooled centrifugal chilling packages | Equipment not designed for operation at AHRI Standard 550/590 test conditions of 44°F leaving and 54°F entering chilled-fluid temperatures and with 85°F entering and 94.3°F leaving condenser fluid temperatures shall have maximum full-load kW/ton and part-load ratings requirements adjusted using the following equations: FLadj = FL /K adj (Equation 4-5) PLVadj = IPLV.IP/Kadj (Equation 4-6)
C403.3.2.2 |  | Positive displacement (air- and water-cooled) chilling packages | Equipment with a leaving fluid temperature higher than 32°F and water-cooled positive displacement chilling packages with a condenser leaving fluid temperature below 115°F shall meet the requirements of the tables in Section C403.3.2 when tested or certified with water at standard rating conditions, in accordance with the referenced test procedure. | [6 empty] | Table C403.3.2(1) | Table C403.3.2(2) | Table C403.3.2(3) | Table C403.3.2(4) | Table C403.3.2(5) | Table C403.3.2(6) | Table C403.3.2(7) | Table C403.3.2(8) | Table C403.3.2(9) | Table C403.3.2(10) | Table C403.3.2(11) | Table C403.3.2(12) | Table C403.3.2(13) | Table C403.3.2(14) | Table C403.3.2(15) | Table C403.3.2(16)
C403.4.1 |  | Thermostatic controls | The supply of heating and cooling energy to each zone shall be controlled by individual thermostatic controls capable of responding to temperature within the zone.
C403.4.1.1 |  | Climate-Appropriate Equipment | Equipment that provides heating and cooling shall be able to adequately function in Boulder’s climate zone, including demonstrated performance of at least 70 percent capacity with outdoor temperatures of 5°F.
C403.4.1.2 |  | Heat pump supplementary heat | Heat pumps having supplementary electric resistance heat shall have controls that limit supplemental heat operation to only those times when one of the following applies: 1. The vapor compression cycle cannot provide the necessary heating energy to satisfy the thermostat setting. 2. The heat pump is operating in defrost mode. 3. The vapor compression cycle malfunctions. 4. The thermostat malfunctions.
C403.4.1.3 |  | Deadband | Where used to control both heating and cooling, zone thermostatic controls shall be configured to provide a temperature range or deadband of not less than 5°F within which the supply of heating and cooling energy to the zone is shut off or reduced to a minimum.
C403.4.1.4 |  | Setpoint overlap restriction | Where a zone has a separate heating and a separate cooling thermostatic control located within the zone, a limit switch, mechanical stop or direct digital control system with software programming shall be configured to prevent the heating setpoint from exceeding the cooling setpoint and to maintain a deadband in accordance with Section C403.4.1.3.
C403.4.1.5 |  | Heated or cooled vestibules | The heating system for heated vestibules and air curtains with integral heating shall be provided with controls configured to shut off the source of heating when the outdoor air temperature is greater than 45°F.
C403.4.1.6 |  | Hot water boiler outdoor temperature setback control | Hot water boilers that supply heat to the building through one- or two-pipe heating systems shall have an outdoor setback control that lowers the boiler water temperature based on the outdoor temperature.
C403.4.1.7 |  | Mechanical system shutoff | Operable wall or roof openings, overhead doors, cargo doors, sliding doors, folding and accordion-style wall systems, and other loading dock-style doors that open to the outdoors shall be equipped with interlock controls that disable the heating, cooling and humidity control equipment that serves the area or zone adjacent to the opening.
C403.4.2 |  | Off-hour controls | Each zone shall be provided with thermostatic setback controls that are controlled by either an automatic time clock or programmable control system.
C403.4.2.1 |  | Thermostatic setback | Thermostatic setback controls shall be configured to set back or temporarily operate the system to maintain zone temperatures down to 55°F or up to 85°F.
C403.4.2.2 |  | Automatic setback and shutdown | Automatic time clock or programmable controls shall be capable of starting and stopping the system for seven different daily schedules per week and retaining their programming and time setting during a loss of power for not fewer than 10 hours.
C403.4.2.3 |  | Automatic start and stop | Automatic start controls shall be provided for each HVAC system. The automatic start controls shall be configured to automatically adjust the daily start time of the HVAC system in order to bring each space to the desired occupied temperature immediately prior to scheduled occupancy. Automatic stop controls shall be provided for each HVAC system with direct digital control of individual zones. The automatic stop controls shall be configured to reduce the HVAC system’s heating temperature setpoint and increase the cooling temperature setpoint by not less than 2°F (-16.6ºC) before scheduled unoccupied periods based on the thermal lag and acceptable drift in space temperature that is within comfort limits.
C403.5 | Economizers | Economizer | An air or water economizer shall be provided for the following cooling systems: 1. Chilled water systems with a total cooling capacity, less cooling capacity provided with air economizers: 1,320,000 Btu/h for Water-cooled Chilled-water Systems or 1,720,000 Btu/h for Air-cooled Chilled-water Systems. 2. Individual fan systems with cooling capacity greater than or equal to 36,000 Btu/h in buildings having other than a Group R occupancy. The total supply capacity of all fan cooling units not provided with economizers shall not exceed 20 percent of the total supply capacity of all fan cooling units in the building or 300,000 Btu/h, whichever is greater. 3. Individual fan systems with cooling capacity greater than or equal to 270,000 Btu/h in buildings having a Group R occupancy. The total supply capacity of all fan cooling units not provided with economizers shall not exceed 20 percent of the total supply capacity of all fan cooling units in the building or 1,500,000 Btu/h, whichever is greater. 4. Provide exception documentation, if applicable.
C403.5.1 |  | Integrated economizer control | Economizer systems shall be integrated with the mechanical cooling system and be configured to provide partial cooling even where additional mechanical cooling is required to provide the remainder of the cooling load. Units that include an air economizer shall comply with the following: 1. Unit controls shall have the mechanical cooling capacity control interlocked with the air economizer controls such that the outdoor air damper is at the 100-percent open position when mechanical cooling is on and the outdoor air damper does not begin to close to prevent coil freezing due to minimum compressor run time until the leaving air temperature is less than 45°F (7°C). 2. Direct expansion (DX) units that control 75,000 Btu/ h (22 kW) or greater of rated capacity of the capacity of the mechanical cooling directly based on occupied space temperature shall have not fewer than two stages of mechanical cooling capacity. 3. Other DX units, including those that control space temperature by modulating the airflow to the space, shall be in accordance with Table C403.5.1. | [6 empty] | Table C403.5.1
C403.5.2 |  | Economizer heating system impact | HVAC system design and economizer controls shall be such that economizer operation does not increase building heating energy use during normal operation. Provide exception documentation, if applicable.
C403.5.3 | Air economizers | Design capacity | Air economizer systems shall be configured to modulate outdoor air and return air dampers to provide up to 100 percent of the design supply air quantity as outdoor air for cooling
|  | Control signal | Economizer controls and dampers shall be configured to sequence the dampers with the mechanical cooling equipment and shall not be controlled by only mixed-air temperature Provide exception documentation, if applicable.
|  | High-limit shutoff | Air economizers shall be configured to automatically reduce outdoor air intake to the design minimum outdoor air quantity when outdoor air intake will not reduce cooling energy usage. High-limit shutoff control types and settings shall be chosen from the following: Fixed dry bulb: Economizer off when Outdoor air temperature exceeds 75°F. Differential dry bulb: Economizer off when Outdoor air temperature exceeds return air temperature. Differential enthalpy with fixed dry-bulb: Economizer off when Outdoor air enthalpy exceeds return air enthalpy OR Outdoor air temperature exceeds 75°F.
|  | Relief of excess outdoor air system | Systems shall be capable of relieving excess outdoor air during air economizer operation to prevent over pressurizing the building. The relief air outlet shall be located to avoid recirculation into the building.
|  | Economizer dampers | Return, exhaust/ relief and outdoor air dampers used in economizers shall comply with AMCA 500D. The dampers shall have an air leakage rate not greater than 4 cfm/ft2 of damper surface area at 1.0 inch water gauge and shall be labeled by an approved agency when tested in accordance with AMCA 500D for such purpose. Outdoor air intake and exhaust dampers shall be installed with automatic controls configured to close when the systems or spaces served are not in use or during unoccupied period warm-up and setback operation.
C403.5.4 | Water-side economizers | Design capacity | Water economizer systems shall be configured to cool supply air by indirect evaporation and providing up to 100 percent of the expected system cooling load at outdoor air temperatures of not greater than 50°F dry bulb/45°F wet bulb. Provide exception documentation, if applicable.
|  | Maximum pressure drop | Precooling coils and water-to-water heat exchangers used as part of a water economizer system shall either have a waterside pressure drop of less than 15 feet (45 kPa) of water or a secondary loop shall be created so that the coil or heat exchanger pressure drop is not seen by the circulating pumps when the system is in the normal cooling (noneconomizer) mode.
C403.5.5 | Economizer fault detection and diagnostics | FDD | Air-cooled unitary direct-expansion units listed in the tables in Section C403.3.2 and variable refrigerant flow (VRF) units that are equipped with an economizer in accordance with Sections C403.5 through C403.5.4 shall include a fault detection and diagnostics system in accordance with Section C403.5.5. | [6 empty] | Table C403.3.2(1) | Table C403.3.2(2) | Table C403.3.2(3) | Table C403.3.2(4) | Table C403.3.2(5) | Table C403.3.2(6) | Table C403.3.2(7) | Table C403.3.2(8) | Table C403.3.2(9) | Table C403.3.2(10) | Table C403.3.2(11) | Table C403.3.2(12) | Table C403.3.2(13) | Table C403.3.2(14) | Table C403.3.2(15) | Table C403.3.2(16)
C403.7.1 | Demand control ventilation |  | Demand control ventilation (DCV) shall be provided for all single-zone systems required to comply with Sections C403.5 through C403.5.3 and spaces larger than 500 square feet and with an average occupant load of 15 people or greater per 1,000 square feet of floor area.
C403.7.3 | Enclosed parking garage ventilation controls |  | Enclosed parking garages used for storing or handling automobiles operating under their own power shall employ carbon monoxide detectors applied in conjunction with nitrogen dioxide detectors and automatic controls configured to stage fans or modulate fan average airflow rates to 50 percent or less of design capacity, or intermittently operate fans less than 20 percent of the occupied time or as required to maintain acceptable contaminant levels in accordance with International Mechanical Code provisions. Failure of contamination-sensing devices shall cause the exhaust fans to operate continuously at design airflow.
C403.7.4 | Ventilation air heating control |  | Units that provide ventilation air to multiple zones and operate in conjunction with zone heating and cooling systems shall not use heating or heat recovery to warm supply air to a temperature greater than 60°F when representative building loads or outdoor air temperatures indicate that the majority of zones require cooling.
C403.7.5 | Energy recovery systems |  | Energy recovery ventilation systems shall be provided as specified in either Section C403.7.5.1 or C403.7.5.2, as applicable. Nontransient dwelling units shall be provided with outdoor air energy recovery ventilation systems with an enthalpy recovery ratio of not less than 60 percent at heating design condition. Where the supply airflow rate of a fan system serving a space other than a nontransient dwelling unit exceeds the values specified in Table C403.7.4.2, the system shall include an energy recovery system. | [6 empty] | Table C403.7.4.2
C403.7.6 | Kitchen exhaust systems |  | Replacement air introduced directly into the exhaust hood cavity shall not be greater than 10 percent of the hood exhaust airflow rate.
C403.7.7 | Automatic control of HVAC systems serving guestrooms |  | In Group R-1 buildings containing more than 50 guestrooms, each guestroom shall be provided with controls complying with the provisions of Sections C403.7.6.1 and C403.7.6.2. Card key controls comply with these requirements.
C403.7.8 | Shutoff dampers |  | Outdoor air intake and exhaust openings and stairway and shaft vents shall be provided with Class I motorized dampers. The dampers shall have an air leakage rate not greater than 4 cfm/ft2 of damper surface area at 1.0 inch water gauge (249 Pa) and shall be labeled by an approved agency when tested in accordance with AMCA 500D for such purpose.
C403.8.1 | Allowable fan horsepower |  | Each HVAC system having a total fan system motor nameplate horsepower exceeding 5 hp (3.7 kW) at fan system design conditions shall not exceed the allowable fan system motor nameplate hp (Option 1) or fan system bhp (Option 2) shown in Table C403.8.1(1). This includes supply fans, exhaust fans, return/relief fans, and fan-powered terminal units associated with systems providing heating or cooling capability. Single-zone variable air volume systems shall comply with the constant volume fan power limitation. | [6 empty] | Table C403.8.1(1)
C403.8.2 | Motor nameplate horsepower |  | For each fan, the fan brake horsepower shall be indicated on the construction documents and the selected motor shall be not larger than the first available motor size greater than the following: 1. For fans less than 6 bhp (4476 W), 1.5 times the fan brake horsepower. 2. For fans 6 bhp (4476 W) and larger, 1.3 times the fan brake horsepower.
C403.8.3 | Fan efficiency |  | Each fan and fan array shall have a fan energy index (FEI) of not less than 1.00 at the design point of operation, as determined in accordance with AMCA 208 by an approved, independent testing laboratory and labeled by the manufacturer. Each fan and fan array used for a variable-air-volume system shall have an FEI of not less than 0.95 at the design point of operation as determined in accordance with AMCA 208 by an approved independent testing laboratory and labeled by the manufacturer. The FEI for fan arrays shall be calculated in accordance with AMCA 208 Annex C.
C403.8.4 | Fractional hp fan motors |  | Motors for fans that are not less than 1/12 hp (0.062 kW) and less than 1 hp (0.746 kW) shall be electronically commutated motors or shall have a minimum motor efficiency of 70 percent, rated in accordance with DOE 10 CFR 431.
C403.11 | Refrigeration equipment performance |  | Refrigeration equipment performance shall be determined in accordance with Sections C403.11.1 and C403.11.2 for commercial refrigerators, freezers, refrigerator-freezers, walk-in coolers, walk-in freezers and refrigeration equipment. The energy use shall be verified through certification under an approved certification program or, where a certification program does not exist, the energy use shall be supported by data furnished by the equipment manufacturer.
C403.12 | Construction of HVAC system elements |  | Ducts, plenums, piping and other elements that are part of an HVAC system shall be constructed and insulated in accordance with Sections C403.12.1 through C403.12.4.1.
C403.12.4 | Piping insulation |  | Piping serving as part of a heating or cooling system shall be thermally insulated in accordance with Table C403.12.4. | [6 empty] | Table C403.12.4
C403.13 | Mechanical systems located outside of the building thermal envelope |  | Mechanical systems providing heat outside of the thermal envelope of a building shall comply with Sections C403.13.1 through C403.13.3
C404.9 | Drainwater heat recovery units |  | Drain water heat recovery units shall comply with CSA B55.2. Potable water-side pressure loss shall be less than 10 psi at maximum design flow. For Group R occupancies, the efficiency of drain water heat recovery unit efficiency shall be in accordance with CSA B55.1.
ELECTRICAL POWER & LIGHTING SYSTEMS
C405.1.1 | Lighting for dwelling units |  | Dwelling units shall comply with Section R404.1.
C405.2.1 | Occupant sensor controls |  | Occupant sensor controls shall be installed to control lights in the following space types: 1. Classrooms/lecture/training rooms. 2. Conference/meeting/multipurpose rooms. 3. Copy/print rooms. 4. Lounges/breakrooms. 5. Enclosed offices. 6. Open plan office areas. 7. Restrooms. 8. Storage rooms. 9. Locker rooms. 10. Corridors. 11. Warehouse storage areas. 12. Other spaces 300 square feet (28 m2) or less that are enclosed by floor-to-ceiling height partitions.
C405.2.2 | Time-switch controls |  | Each area of the building that is not provided with occupant sensor controls complying with Section C405.2.1.1 shall be provided with time-switch controls complying with Section C405.2.2.1.
C405.2.3 | Light-reduction controls |  | Where not provided with occupant sensor controls complying with Section C405.2.1.1, general lighting shall be provided with light-reduction controls complying with Section C405.2.3.1.
C405.2.4 | Daylight-responsive controls |  | Daylight-responsive controls complying with Section C405.2.4.1 shall be provided to control the general lighting within daylight zones in the following spaces: 1. Spaces with a total of more than 150 watts of general lighting within primary sidelit zones complying with Section C405.2.4.2. 2. Spaces with a total of more than 300 watts of general lighting within sidelit daylight zones complying with Section C405.2.4.2. 3. Spaces with a total of more than 150 watts of general lighting within toplit daylight zones complying with Section C405.2.4.3.
C405.2.7 | Exterior lighting controls |  | Exterior lighting systems shall be provided with controls that comply with Sections C405.2.7.1 through C405.2.7.4.
C405.2.7 | Parking garage lighting control |  | Lighting for parking garages shall have controls that comply with C405.2.7
C405.3 | Interior lighting power requirements |  | A building complies with this section when its total connected interior lighting power calculated under Section C405.3.1 is not greater than the interior lighting power allowance calculated under Section C405.3.2. Indicate if Building Area Method or Space-by-Space Method is used to determine Lighting Power Allowance and included project specific lighting calculations demonstrating compliance on the Lighting Calculations Tab Note: select the Boulder 2024 Code on the Project Tab. | [6 empty] | Lighting Calculations
C405.4 | Horticultural lighting requirements |  | Not less than 95 percent of the permanently installed luminaires for horticultural lighting shall have a photosynthetic photon of not less than 1.7 µmol/J in greenhouses and not less than 1.9 umol/J for all other horticultural lighting. Luminaires for horticultural lighting shall be controlled by a device that that can be programmed to turn on at specific times and that can automatically turn off the luminaire when sufficient daylight is available.
C405.5 | Exterior lighting power requirements |  | A building complies with this section when its total connected exterior lighting power calculated in accordance with Section C405.5.1 shall be not greater than the exterior lighting power allowance calculated in accordance with Section C405.5.2. Indicate the lighting zone along with the BOBECC area type determine the allowable Lighting Power Density. Included project specific lighting calculations demonstrating compliance on the Lighting Calculations Tab Note: select the Boulder 2024 Code on the Project Tab.
C405.6 | Dwelling electrical meter |  | Each dwelling unit located in a Group R-2 building shall have a separate electrical meter.
C405.7 | Electrical transformers |  | Low-voltage dry-type distribution electric transformers shall meet the minimum efficiency requirements of Table C405.7 as tested and rated in accordance with the test procedure listed in DOE 10 CFR 431. The efficiency shall be verified through certification under an approved certification program or, where a certification program does not exist, the equipment efficiency ratings shall be supported by data furnished by the transformer manufacturer. | [6 empty] | Table C405.7
C405.12 | Energy Monitoring |  | New buildings with a gross conditioned floor area of 25,000 square feet or larger shall be equipped to measure, monitor, record and report energy consumption data in compliance with Sections C405.12.1 through C405.12.5.
ELECTRIC-READY BUILDINGS
C405.20 | Electric ready |  | These provisions shall be applicable for all new buildings, additions and first tenant finish permits that utilize combustion equipment. In the event of a first tenant finish to a commercial core and shell building or unfinished space is credited towards meeting the requirements of this chapter, the code official shall not issue a certificate of occupancy to the tenant until the requirements of Section C405.20.1 or C405.20.2 have met as applicable.
C405.20.1.2/ C405.20.2.2 | Electrical panel space |  | The electrical panel shall have reserved physical space for a minimum two-pole or three-pole circuit breaker for each branch circuit provided for future electric equipment or appliances. The physical space in the electrical panel for each circuit breaker shall be sized with sufficient breaker capacity to meet the electrical demand of the future electric equipment or appliance that is sized to serve a comparable capacity to meet the heating load.
SOLAR-READY BUILDINGS
C405.15 | Solar-ready zone |  | The solar-ready zone shall have a minimum total area described as follows. The solar-ready zone shall comply with access, pathway, smoke ventilation, and spacing requirements as specified in the Boulder Revised Code. The solar-ready zone total area shall be comprised of one or more rectangular areas. For sloped roofs each area must be not less than 200 square feet and no side of any rectangular area shall be less than 11 feet in length. For low-sloped or flat roofs, each area must be not less than 330 square feet, with a minimum length running generally north to south of 15' and a minimum length running generally east to west of 22'and no side of any rectangular area shall be less than 11 feet in length
C405.15.2 | Orientation |  | All sections of the solar zone located on steep sloped roofs shall be oriented between 110 degrees and 270 degrees of true north.
C405.15.3 | Obstructions |  | No obstructions, including, but not limited to, vents, chimneys, architectural features, and roof-mounted equipment, shall be located in the solar zone.
C405.15.4 | Roof loads and documentation |  | The structural design loads for roof dead load and roof live load shall be clearly indicated on the construction documents.
C405.16 | Interconnection pathways |  | The construction documents shall indicate at least one potential pathway for routing of conduit and/or raceway from the solar-ready zone to the point of interconnection with the an electrical service panel and electrical storage system area.
C405.18 | Electrical services reserved space |  | The main electrical service panel shall have a minimum bus bar rating of not less than 200 amps. The main electrical service panel shall have reserved spaces to allow for the installation of double pole circuit breakers for a future solar electric installation and a double pole circuit breaker for future electrical storage system installation. The reserved spaces shall be positioned at the opposite (load) end from the input feeder location or main circuit location. The reserved spaces shall be permanently marked as “For Future Solar Electric and Storage.”. The minimum reserved amperage shall be determined from Table C405.18. | [6 empty] | Table C405.18
ELECTRIC VEHICLES
C405.13 | Electric Vehicles |  | The building shall be provided with electric vehicle (EV) charging in accordance with this section and the National Electrical Code (NFPA 70). Where parking spaces are added or modified without an increase in building size, only the new parking spaces are subject to this requirement. The number of required EVSE installed spaces, EV ready spaces, EV capable spaces, and EV capable light spaces shall be determined based on the total number of provided vehicle parking spaces or the number of vehicle parking spaces required under Section 9-9-6, “Parking Standards,” B.R.C. 1981 prior to any approved parking reductions.
SYSTEM COMMISSIONING
C408.2 | Mechanical systems and service water-heating systems commissioning and completion requirements |  | Prior to the final mechanical and plumbing inspections, the registered design professional or approved agency shall provide evidence of mechanical systems commissioning and completion in accordance with the provisions of this section. | [5 empty] | Building Condition: Commissioning
C408.3.1 | Functional testing of lighting controls |  | Prior to passing final inspection, the registered design professional or approved agency shall provide evidence that the lighting control systems have been tested to ensure that control hardware and software are calibrated, adjusted, programmed and in proper working condition in accordance with the construction documents and manufacturer’s instructions. Functional testing shall be in accordance with Sections C408.3.1.1 through C408.3.1.3 for the applicable control type. | [5 empty] | Building Condition: Commissioning

## Lighting Calculations
2024 Boulder Energy Code - Commercial Lighting Calculations | [6 empty] | 2024 City of Boulder Energy Conservation Code
INTERIOR LIGHTING
Space-by-Space Method Directions: 1. List all unique space types per the 2024 City of Boulder Energy Conservation Code Table C405.3.2(2). 2. Identify space type from the drop down menu. 3. Indicate space square footage. 4. List all proposed lighting fixtures including existing-to-remain fixtures. 4. Identify number of fixtures per space. 5. For watts per fixture enter the luminaire wattage for installed lamp and ballast using manufacturer's data.
ROOM Number | COBECC Space Type | Space SQ FT | COBECC LPD (w/SF) | Allowable Watts | Fixture Type | Number of Fixtures | Watts per Fixture | Designed Watts | Designed LPD (w/SF)
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
(add rows as needed) |  |  | -
Total Designed Watts must be less than Total Allowable Watts |  |  |  | 0 |  |  |  | 0
Building Area Method Directions: 1. List building levels and sqare footages. 2. Identify COBECC LPD based on the 2024 City of Boulder Energy Conservation Code Table C405.3.2(1). 3. List all proposed lighting fixtures including existing-to-remain fixtures. 4. Identify number of fixtures per space. 5. For watts per fixture enter the luminaire wattage for installed lamp and ballast using manufacturer's data.
Building Level | COBECC Building Area Type | Area SQ FT | COBECC LPD (w/SF) | Allowable Watts | Fixture Type | Number of Fixtures | Watts per Fixture | Designed Watts
|  |  | - | -
|  |  | - | -
|  |  | - | -
|  |  | - | -
|  |  | - | -
(add rows as needed) |  |  | - | -
Total Designed Watts must be less than Total Allowable Watts |  |  |  | 0 |  |  |  | 0
2024 Boulder Energy Code - Commercial Lighting Calculations | [6 empty] | 2024 City of Boulder Energy Conservation Code
EXTERIOR LIGHTING
Directions: 1. Determine the Lighting Zone (LZ) for the building (1-4) and SELECT from the dropdown. 2. Identify all exterior lighted area types from the drop down menu. 3. Indicate the square footage (or length) for all exterior areas illuminated by lighting powered by the building's energy service. 4. List all proposed lighting fixtures including existing-to-remain fixtures. 4. Identify number of fixtures per area. 5. For watts per fixture enter the luminaire wattage for installed lamp and ballast using manufacturer's data.
Lighting Zone: |  |  | Base Allowance: | -
Location Description | COBECC Area Type | Area SQ FT (or length) or Each | COBECC LPD (w/SF) | Allowable Watts | Fixture Type | Number of Fixtures | Watts per Fixture | Designed Watts
|  |  | - | -
|  |  | - | -
|  |  | - | -
|  |  | - | -
|  |  | - | -
|  |  | - | -
|  |  | - | -
|  |  | - | -
|  |  | - | -
|  |  | - | -
|  |  | - | -
|  |  | - | -
|  |  | - | -
|  |  | - | -
(add rows as needed) |  |  | - | -
NON-TRADABLE | [9 empty] | Nontradable Excess
|  |  | - | - | [5 empty] | #VALUE!
|  |  | - | - | [5 empty] | #VALUE!
|  |  | - | - | [5 empty] | #VALUE!
(add rows as needed) |  |  | - | - | [5 empty] | #VALUE!
Non-Tradable Wattage Excess |  |  |  | 0
Total Designed Watts must be less than Total Allowable Watts |  |  |  | 0 |  |  |  | 0
| Base | 160 | 280 | 400 | 560
|  | 1 | 2 | 3 | 4
| Uncovered Parking Areas - Parking Areas and drives | 0.015 | 0.026 | 0.037 | 0.052
| Building Grounds - Walkways/ramps <10ft wide | 0.5 | 0.5 | 0.55 | 0.6
| Building Grounds - Walkways/ramps ≥10ft wide (including plaza areas, speacial featrue areas) | 0.1 | 0.1 | 0.11 | 0.14
| Building Grounds - Dining Areas | 0.156 | 0.273 | 0.39 | 0.546
| Building Grounds - Stairways | 0.6 | 0.7 | 0.7 | 0.7
| Building Grounds - Pedestrian tunnels | 0.063 | 0.11 | 0.14 | 0.21
| Building Grounds - Landscaping | 0.014 | 0.025 | 0.036 | 0.04
| Building Entrances and Exits - Pedestrian and vehecular entrances and exits (Lf of opening) | 5.6 | 9.8 | 14 | 19.6
| Building Entrances and Exits - Entry canopies | 0.072 | 0.126 | 0.18 | 0.252
| Building Entrances and Exits - Loading docks | 0.104 | 0.182 | 0.26 | 0.35
| Sales Canopies - Free standing and attached | 0.2 | 0.35 | 0.5 | 0.7
| Outdoor Sales - Open area (including vehicle sales lots) | 0.072 | 0.126 | 0.18 | 0.252
| Outdoor Sales - Street Frontage for vehicle sales lots in addition to 'open area' allowance | 0 | 7 | 7 | 14.4
| Non-tradable - Building facades (Sqft or Lf) | 0 | 0.075 | 0.113 | 0.15
| Non-tradable - ATMs and night depositories (plus 35 W per each extra) | 90 | 90 | 90 | 90
| Non-tradable - Uncovered entrances and gatehouse inspection stations at guarded facilites | 0.144 | 0.252 | 0.36 | 0.504
| Non-tradable - Uncovered loading areas for law enforcement, fire, ambulance and other emergency services vehicles | 0.104 | 0.182 | 0.26 | 0.364
| Non-tradable - Drive-up windows and doors (Per each) | 52 | 92 | 132 | 185
| Non-tradable - Parking near 24-hr retail entrances (Per each) | 80 | 140 | 200 | 280
BUILDING AREA | BUILDING AREA TYPE | LPD (w/ft2)
METHOD | Automotive facility | 0.64
| Convention center | 0.64
| Courthouse | 0.74
| Dining: bar lounge/leisure | 0.69
| Dining: cafeteria/fast food | 0.66
| Dining: family | 0.61
| Dormitory | 0.52
| Exercise center | 0.65
| Fire stationa | 0.5
| Gymnasium | 0.65
| Health care clinic | 0.68
| Hospitala | 0.86
| Hotel/Motel | 0.53
| Library | 0.7
| Manufacturing facility | 0.6
| Motion picture theater | 0.44
| Multifamilyc | 0.45
| Museum | 0.55
| Office | 0.62
| Parking garage | 0.12
| Penitentiary | 0.65
| Performing arts theater | 0.82
| Police station | 0.64
| Post office | 0.62
| Religious building | 0.66
| Retail | 0.78
| School/university | 0.65
| Sports arena | 0.73
| Town hall | 0.67
| Transportation | 0.5
| Warehouse | 0.41
| Workshop | 0.83
SPACE BY SPACE | SPACE TYPES |  |  |  | LPD (watts/sq ft)
METHOD | Atrium - Less than 40 feet in height |  |  |  | 0.41
| Atrium - Greater than 40 feet in height |  |  |  | 0.51
| Audience seating area - In an auditorium |  |  |  | 0.57
| Audience seating area - In a convention center |  |  |  | 0.65
| Audience seating area - In a gymnasium |  |  |  | 0.23
| Audience seating area - In a motion picture theater |  |  |  | 0.27
| Audience seating area - In a penitentiary |  |  |  | 0.56
| Audience seating area - In a performing arts theater |  |  |  | 1.1
| Audience seating area - In a religious building |  |  |  | 0.72
| Audience seating area - In a sports arena |  |  |  | 0.27
| Audience seating area - Otherwise |  |  |  | 0.23
| Banking activity area |  |  |  | 0.56
Breakroom (See Lounge/breakroom)
| Classroom/lecture hall/training room - In a penitentiary |  |  |  | 0.74
| Classroom/lecture hall/training room - Otherwise |  |  |  | 0.71
| Computer room |  |  |  | 0.75
| Conference/meeting/multipurpose room |  |  |  | 0.88
| Confinement cells |  |  |  | 0.51
| Copy/print room |  |  |  | 0.31
| Corridor - In a facility for the visually impaired (and not used primarily by the staff) |  |  |  | 0.71
| Corridor - In a hospital |  |  |  | 0.61
| Corridor - In a manufacturing facility |  |  |  | 0.28
| Corridor - In a primary or secondary school (and not used primarily by the staff) |  |  |  | 0.71
| Corridor - Otherwise |  |  |  | 0.41
| Courtroom |  |  |  | 1.06
| Dining area - In bar/lounge or leisure dining |  |  |  | 0.62
| Dining area - In cafeteria or fast food dining |  |  |  | 0.36
| Dining area - In a facility for the visually impaired (and not used primarily by the staff) Electrical/mechanical room Emergency vehicle garage |  |  |  | 1.22
| Dining area - In family dining |  |  |  | 0.52
| Dining area - In a penitentiary |  |  |  | 0.35
| Dining area - Otherwise |  |  |  | 0.42
| Dwelling unit |  |  |  | 0.43
| Electrical/mechanical room |  |  |  | 0.39
| Emergency vehicle garage |  |  |  | 0.41
| Food preparation area |  |  |  | 0.92
| Guestroom |  |  |  | 0.41
| Laboratory - In or as a classroom |  |  |  | 1.04
| Laboratory - Otherwise |  |  |  | 1.21
| Laundry/washing area |  |  |  | 0.43
| Loading dock, interior |  |  |  | 0.51
| Lobby - For an elevator |  |  |  | 0.52
| Lobby - In a facility for the visually impaired (and not used primarily by the staff) |  |  |  | 1.44
| Lobby - In a hotel |  |  |  | 0.48
| Lobby - In a motion picture theater |  |  |  | 0.2
| Lobby - In a performing arts theater |  |  |  | 0.82
| Lobby - Otherwise |  |  |  | 0.8
| Locker room |  |  |  | 0.43
| Lounge/breakroom - In a healthcare facility |  |  |  | 0.42
| Lounge/breakroom - Otherwise |  |  |  | 0.44
| Office - Enclosed |  |  |  | 0.73
| Office - Open plan |  |  |  | 0.56
| Parking area, interior |  |  |  | 0.11
| Pharmacy area |  |  |  | 1.23
| Restroom - In a facility for the visually impaired (and not used primarily by the staff) |  |  |  | 0.96
| Restroom - Otherwise |  |  |  | 0.63
| Sales area |  |  |  | 0.85
| Seating area, general |  |  |  | 0.21
| Stairway (see Space containing stairway) |  |  |  | 0
| Stairwell |  |  |  | 0.47
| Storage room |  |  |  | 0.38
| Vehicular maintenance area |  |  |  | 0.53
| Workshop |  |  |  | 1.09
| Automotive (see Vehicular maintenance area) |  |  |  | 0
| Convention Center—exhibit space |  |  |  | 0.5
| Dormitory—living quarters |  |  |  | 0.43
| Facility for the visually impaired - In a chapel (and not used primarily by the staff) |  |  |  | 0.58
| Facility for the visually impaired - In a recreation room (and not used primarily by the staff) |  |  |  | 1.2
| Fire Station—sleeping quarters |  |  |  | 0.19
| Gymnasium/fitness center - In an exercise area |  |  |  | 0.5
| Gymnasium/fitness center - In a playing area |  |  |  | 0.75
| Healthcare facility - In control room (MRI/CT/radiology/PET) |  |  |  | 0.78
| Healthcare facility - In an exam/treatment room |  |  |  | 1.16
| Healthcare facility - In an imaging room |  |  |  | 0.94
| Healthcare facility - In a medical supply room |  |  |  | 0.54
| Healthcare facility - In a nursery |  |  |  | 0.87
| Healthcare facility - In a nurse’s station |  |  |  | 0.75
| Healthcare facility - In an operating room |  |  |  | 1.87
| Healthcare facility - In a patient room |  |  |  | 0.45
| Healthcare facility - In a physical therapy room |  |  |  | 0.82
| Healthcare facility - In a recovery room |  |  |  | 0.89
| Library - In a reading area |  |  |  | 0.77
| Library - In the stacks |  |  |  | 1.18
| Manufacturing Facility - In a detailed manufacturing area |  |  |  | 0.75
| Manufacturing Facility - In an equipment room |  |  |  | 0.61
| Manufacturing Facility - In an extra-high-bay area(> 50 floor-to-ceiling height) |  |  |  | 0.73
| Manufacturing Facility - In a high-bay area (25-50 floor-to-ceiling height) |  |  |  | 0.58
| Manufacturing Facility - In a low-bay area (less than 25 floor-to- ceiling height) |  |  |  | 0.61
| Museum - In a general exhibition area |  |  |  | 0.31
| Museum - In a restoration room |  |  |  | 0.77
| Performing arts theater—dressing room |  |  |  | 0.35
| Post office—sorting area |  |  |  | 0.66
| Religious buildings - In a fellowship hall |  |  |  | 0.5
| Religious buildings - In a worship/pulpit/choir area |  |  |  | 0.75
| Retail facilities - In a dressing/fitting room |  |  |  | 0.45
| Retail facilities - In hair care salon |  |  |  | 0.65
| Retail facilities - In nail care salon |  |  |  | 0.75
| Retail facilities - In massage clinic |  |  |  | 0.81
| Retail facilities - In a mall concourse |  |  |  | 0.57
| Sports arena—playing area - For a Class I facility |  |  |  | 2.26
| Sports arena—playing area - For a Class II facility |  |  |  | 1.45
| Sports arena—playing area - For a Class III facility |  |  |  | 1.08
| Sports arena—playing area - For a Class IV facility |  |  |  | 0.72
| Transportation facility - In a baggage/carousel area |  |  |  | 0.28
| Transportation facility - In an airport concourse |  |  |  | 0.25
| Transportation facility - At a terminal ticket counter |  |  |  | 0.4
| Warehouse—storage area - For medium to bulky, palletized items |  |  |  | 0.33
| Warehouse—storage area - For smaller, hand-carried items |  |  |  | 0.69

## C406.1 Credits
2024 Boulder Energy Code - Commercial Planning Tool for C406.1 2024 Boulder Energy Code Additional Conservation Credits Requirements for New Construction and C502 Additions | [19 empty] | 2024 City of Boulder Energy Conservation Code
Instructions: Enter values in to applicable cells.
Project Background
1. Property is all-electric (Y/N): | Y
2. Project is non-previously-occupied tenant space (Y/N): | Y
Credit Requirements Table C406.1.1 | Floor Area by Building Type (sf) | Boulder Credit Requirements |  |  | Use Group for Table C406.1.1
|  | All-Electric Properties | Mixe Fuel Buildings
Multifamily, Hotel/Motel, Assisted Living Faciltiies |  | 65 | 105 |  | Group R-2, R-4, I-1
Healthcare/Hospital |  | 18 | 58 |  | Group I-2
Restaurants/Food Halls |  | 47 | 87 |  | Group A-2
Office |  | 58 | 98 |  | Group B
Retail |  | 62 | 87 |  | Group M
School |  | 42 | 92 |  | Group E
Warehouse |  | 57 | 97 |  | Group S-2, S-1
All Other |  | 0 | 40 |  | Other Occupancies
Total Floor Area | 0
Total Area Weighted Boulder Credit Requirements (All-Electric) | #DIV/0!
Total Area Weighted Boulder Credit Requirements (Mixed Fuel) | 0
Mark "Y" in peach-colored cell if credit is included for each of the following building types -----> |  |  | R-2, R-4, and I-1 |  | I-2 |  | B |  | A-2 |  | M |  | E |  | S-1,S-2 |  | Other
Code Section | Included in COMcheck IECC-2021 OR Boulder Specific |  | Enter Y if included | Boulder Credits | Enter Y if included | Boulder Credits | Enter Y if included | Boulder Credits | Enter Y if included | Boulder Credits | Enter Y if included | Boulder Credits | Enter Y if included | Boulder Credits | Enter Y if included | Boulder Credits | Enter Y if included | Boulder Credits | Notes | Documentation
C406.2.1.2: UA Reduction (15%) | COMcheck IECC-2021 |  |  | 15 |  | 3 |  | 6 |  | 7 |  | 11 |  | 6 |  | 21 |  | 10
C406.2.1.3: Envelope Leak Reduction | COMcheck IECC-2021 |  |  | 16 |  | 3 |  | 4 |  | 9 |  | 13 |  | 1 |  | 25 |  | 9
C406.2.1.6: Improved Fenestration | COMcheck IECC-2021 |  |  | 18 |  | 1 |  | 5 |  | 2 |  | 5 |  | 18 |  | 1 |  | 7
C406.2.2.2: Heating Efficiency Improvement | COMcheck IECC-2021 |  |  | 5 |  | 8 |  | 4 |  | 11 |  | 17 |  | 11 |  | 31 |  | 11
C406.2.2.3: Cooling Efficiency Improvement | COMcheck IECC-2021 |  |  | 2 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 0
C406.2.2.4: Residential HVAC Control | Boulder Specific |  |  | 27 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
C406.2.2.5: Dedicated Outdoor Air System Fan Control | Boulder Specific |  |  | 36 |  | 56 |  | 38 |  | 53 |  | 91 |  | 65 |  | 132 |  | 61
C406.2.2.7: Central Space Heating Heat Pump | Boulder Specific |  |  | 30 |  | 30 |  | 30 |  | 30 |  | 30 |  | 30 |  | 30 |  | 30
C406.2.3.1: Recovered/Renew SWH | COMcheck IECC-2021 |  |  | 111 |  | 6 |  | 13 |  | 40 |  | 19 |  | 14 |  | 6 |  | 8
C406.2.3.2: Heat Pump SWH | COMcheck IECC-2021 |  |  | 96 |  | 3 |  | 5 |  | 28 |  | 5 |  | 10 |  | 2 |  | 20
C406.2.3.4: Water heating pipe insulation | COMcheck IECC-2021 |  |  | 8 |  | 1 |  | 4 |  | 3 |  | 4 |  | 5 |  | 2 |  | 23
C406.2.3.5 Point of use (POU) water heaters | Boulder Specific |  |  | 0 |  | 0 |  | 20 |  | 0 |  | 0 |  | 5 |  | 0 |  | 0
C406.2.3.6: Thermostatic Balancing Valve | Boulder Specific |  |  | 3 |  | 1 |  | 1 |  | 1 |  | 1 |  | 2 |  | 1 |  | 4
C406.2.3.7: Heat trace system | Boulder Specific |  |  | 14 |  | 2 |  | 5 |  | 4 |  | 5 |  | 6 |  | 2 |  | 13
C406.2.3.8: Water heating system submeters | Boulder Specific |  |  | 20 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1
C406.2.3.10: Shower drain water heat recovery | Boulder Specific |  |  | 29 |  | 1 |  | 3 |  | 0 |  | 0 |  | 3 |  | 0 |  | 20
C406.2.4.1: Energy Monitoring | COMcheck IECC-2021 |  |  | 2 |  | 3 |  | 0 |  | 2 |  | 5 |  | 3 |  | 5 |  | 54
C406.2.5.2: Enhanced Digital Light Ctrl | COMcheck IECC-2021 |  |  | 1 |  | 5 |  | 6 |  | 2 |  | 7 |  | 5 |  | 6 |  | 3
C406.2.5.3: Increase occupancy sensor | Boulder Specific |  |  | 2 |  | 5 |  | 6 |  | 1 |  | 7 |  | 4 |  | 7 |  | 0
C406.2.5.4: Increase daylight area | COMcheck IECC-2021 with Boulder Specific instructions |  |  | 3 |  | 6 |  | 7 |  | 2 |  | 9 |  | 5 |  | 8 |  | 4
C406.2.5.5: Residential light control | Boulder Specific |  |  | 7 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 5
C406.2.6.2: Efficient Kitchen Equipment | COMcheck IECC-2021 |  |  | 0 |  | 15 |  | 0 |  | 40 |  | 0 |  | 0 |  | 0 |  | 5
C406.3.1: Lighting Load Management | Boulder Specific |  |  | 11 |  | 14 |  | 18 |  | 4 |  | 21 |  | 14 |  | 23 |  | 0
C406.3.2 HVAC Load Management | Boulder Specific |  |  | 11 |  | 22 |  | 31 |  | 31 |  | 1 |  | 31 |  | 13 |  | 0
C406.3.3 Automated Shading Load Management | Boulder Specific |  |  | 13 |  | 2 |  | 10 |  | 0 |  | 10 |  | 15 |  | 0 |  | 0
C406.3.4 Electric Energy Storage | Boulder Specific |  |  | 13 |  | 15 |  | 30 |  | 15 |  | 40 |  | 15 |  | 24 |  | 0
C406.3.5: Cooling Energy Storage | Boulder Specific |  |  | 17 |  | 18 |  | 15 |  | 10 |  | 19 |  | 28 |  | 1 |  | 0
C406.3.7: Building Thermal Mass | Boulder Specific |  |  | 58 |  | 53 |  | 9 |  | 18 |  | 24 |  | 60 |  | 20 |  | 0
C406.3.8: Embodied Carbon Credits | Boulder Specific |  |  | 30 |  | 30 |  | 30 |  | 30 |  | 30 |  | 30 |  | 30 |  | 0
Totals by Building Occupancy Type |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Total Credits Designed |  | 0
| All Electric Building Total Credits Required |  | #DIV/0!
| Mixed Fuel Building Total Credits Required |  | 0

## Table C402.5.2
TABLE C402.5.2
MAXIMUM AIR LEAKAGE RATE FOR FENESTRATION ASSEMBLIES
FENESTRATION ASSEMBLY | MAXIMUM RATE (CFM/FT2) | TEST PROCEDURE
Windows | 0.20 a | AAMA/WDMA/ CSA101/I.S.2/A440 or NFRC 400
Sliding doors | 0.20 a
Swinging doors | 0.20 a
Skylights – with condensation weepage openings | 0.30
Skylights – all other | 0.20 a
Curtain walls | 0.06 | NFRC 400 or ASTM E283 at 1.57 psf (75 Pa)
Storefront glazing | 0.06
Commercial glazed swinging entrance doors | 1.00
Power-operated sliding doors and power- operated folding doors | 1.00
Revolving doors | 1.00
Garage doors | 0.40 | ANSI/DASMA 105, NFRC 400, or ASTM E283 at 1.57 psf (75 Pa)
Rolling doors | 1.00
High-speed doors | 1.30
For SI: 1 cubic foot per minute = 0.47 L/s, 1 square foot = 0.093 m2.
a. The maximum rate for windows, sliding and swinging doors, and skylights is permitted to be 0.3 cfm per square foot of fenestration or door area when tested in accordance with AAMA/WDMA/CSA101/I.S.2/A440 at 6.24 psf (300 Pa).

## Table C402.1.3
TABLE C402.1.3
OPAQUE THERMAL ENVELOPE INSULATION COMPONENT MINIMUM REQUIREMENTS, R-VALUE METHODa

## Table C402.1.4
TABLE C402.1.4
OPAQUE THERMAL ENVELOPE ASSEMBLY MAXIMUM REQUIREMENTS, U-FACTOR METHODa, b
| ALL OTHER | GROUP R
Roofs
Insulation entirely above roof deck | U-0.030 | U-0.030
Metal buildings | U-0.035 | U-0.035
Attic and other | U-0.020 | U-0.020
Walls, above grade
Massf | U-0.086 | U-0.076
Metal building | U-0.048 | U-0.048
Metal framed | U-0.052 | U-0.052
Wood framed and otherc | U-0.048 | 0.042
Walls, below grade
Below-grade wallc | C-0.119 | C-0.092
Floors
Massd | U-0.057 | U-0.051
Joist/framing | U-0.033 | U-0.033
Slab-on-grade floors
Unheated slabs | F-0.52 | F-0.51
Heated slabse | F-0.62 | F-0.62
Opaque doors
Nonswinging doorh | U-0.31 | U-0.31
Swinging doorg | U-0.37 | U-0.37
For SI: 1 pound per square foot = 4.88 kg/m2, 1 pound per cubic foot = 16 kg/ m3.
ci = Continuous insulation, NR = No Requirement, LS = Liner System.
a | Where assembly U-factors, C-factors, and F-factors are established in ANSI/ASHRAE/IESNA 90.1 Appendix A, such opaque assemblies shall be a compliance alternative where those values meet the criteria of this table, and provided that the construction, excluding the cladding system on walls, complies with the appropriate construction details from ANSI/ ASHRAE/ISNEA 90.1 Appendix A.
b | Where U-factors have been established by testing in accordance with ASTM C1363, such opaque assemblies shall be a compliance alternative where those values meet the criteria of this table. The R-value of continuous insulation shall be permitted to be added to or subtracted from the original tested design.
c | Where heated slabs are below grade, below-grade walls shall comply with the U-factor requirements for above-grade mass walls.
d | “Mass floors” shall be in accordance with Section C402.2.3.
e | The first value is for perimeter insulation and the second value is for full, under-slab insulation.
f | “Mass walls” shall be in accordance with Section C402.2.2.
g | Swinging door U-factors shall be determined in accordance with NFRC-100.
h | Garage doors having a single row of fenestration shall have an assembly U-factor less than or equal to 0.44, provided that the fenestration area is not more than 25 percent of the total door area.

## Table C403.3.2(1)
TABLE C403.3.2(1)
MINIMUM EFFICIENCY REQUIREMENTS:
ELECTRICALLY OPERATED UNITARY AIR CONDITIONERS AND CONDENSING UNITS
EQUIPMENT TYPE | SIZE CATEGORY | HEATING SECTION TYPE | SUBCATEGORY OR RATING CONDITION | MINIMUM EFFICIENCY | TEST PROCEDUREa
Air conditioners, air cooled | < 65,000 Btu/h b | All | Split system b
|  |  |  | 13.0 SEERd | before 1/1/2023
13.4 SEER2
AHRI 210/240-2017
|  |  | Single package b | 14.0 SEERd | after 1/1/2023
13.4 SEER2
Space constrained, air cooled |  30,000 Btu/h b | All | Split System and Single Package b | 12.0 SEERd | AHRI 210/240-2023
11.7 SEER2
Small-duct high-velocity, air cooled | < 65,000 Btu/h b | All | Split System b | 12.0 SEERd
12.1 SEER2
Air conditioners, air cooled |  65,000 Btu/h and | Electric Resistance | Split System and Single Package | 11.2 EERd | AHRI 340/360
| < 135,000 Btu/h | (or None) |  | 12.9 IEERd
14.8 IEER
|  | All other |  | 11.0 EERd
12.7 IEERd
14.6 IEER
|  135,000 Btu/h and | Electric Resistance |  | 11.0 EERd
| < 240,000 Btu/h | (or None) |  | 12.4 IEERd
14.2 IEER
|  | All other |  | 10.8 EERd
12.2 IEERd
14.0 IEER
|  240,000 Btu/h and | Electric Resistance | Split System and Single Package | 10.0 EERd
| < 760,000 Btu/h | (or None) |  | 11.6 IEERd
13.2 IEER
|  | All other |  | 9.7 EERd
11.2 IEERd
12.5 IEER
|  760,000 Btu/h | Electric Resistance |  | 9.8 EERd
|  | (or None) |  | 11.4 IEERd
13.0 IEER
|  | All other |  | 9.5 EERd
11.0 IEERd
12.3 IEER
Air conditioners, water cooled | < 65,000 Btu/h b | All | Split System and Single Package | 12.1 EER | AHRI 210/240
12.3 IEER
|  65,000 Btu/h and | Electric Resistance |  | 12.1 EER | AHRI 340/360
| < 135,000 Btu/h | (or None) |  | 13.9 IEER
|  | All other |  | 11.9 EER
13.7 IEER
|  135,000 Btu/h and | Electric Resistance |  | 12.5 EER
| < 240,000 Btu/h | (or None) |  | 13.9 IEER
|  | All other |  | 12.3 EER
13.7 IEER
|  240,000 Btu/h and | Electric Resistance |  | 12.4 EER
| < 760,000 Btu/h | (or None) |  | 13.6 IEER
|  | All other |  | 12.2 EER
13.4 IEER
|  760,000 Btu/h | Electric Resistance |  | 12.2 EER
|  | (or None) |  | 13.5 IEER
|  | All other |  | 12.0 EER
13.3 IEER
Air conditioners, evaporatively cooled | < 65,000 Btu/hb | All | Split System and Single Package | 12.1 EER | AHRI 210/240
12.3 IEER
|  65,000 Btu/h and | Electric Resistance |  | 12.1 EER | AHRI 340/360
| < 135,000 Btu/h | (or None) |  | 12.3 IEER
|  | All other |  | 11.9 EER
12.1 IEER
|  135,000 Btu/h and | Electric Resistance |  | 12.0 EER
| < 240,000 Btu/h | (or None) |  | 12.2 IEER
|  | All other |  | 11.8 EER
12.0 IEER
|  240,000 Btu/h and | Electric Resistance |  | 11.9 EER
| < 760,000 Btu/h | (or None) |  | 12.1 IEER
|  | All other |  | 11.7 EER
11.9 IEER
|  760,000 Btu/h | Electric Resistance |  | 11.7 EER
|  | (or None) |  | 11.9 IEER
|  | All other |  | 11.5 EER
11.7 IEER
Condensing units, air cooled |  135,000 Btu/h | — | — | 10.5 EER | AHRI 365
11.8 IEER
Condensing units, water cooled |  135,000 Btu/h | — | — | 13.5 EER
14.0 IEER
Condensing units, evaporatively cooled |  135,000 Btu/h | — | — | 13.5 EER
14.0 IEER
For SI: 1 British thermal unit per hour = 0.2931 W.
a | Chapter 6 contains a complete specification of the referenced test procedure, including the reference year version of the test procedure.
b | Single-phase, US air-cooled air conditioners less than 65,000 Btu/h are regulated as consumer products by the US Department of Energy Code of Federal Regulations DOE 10 CFR 430. SEER and SEER2 values for single-phase products are set by the US Department of Energy.
c | This table is a replica of ASHRAE 90.1 Table 6.8.1-1 Electrically Operated Unitary Air Conditioners and Condensing Units-Minimum Efficiency Requirements less the values for equipment for applications outside the US.
d | This efficiency value shall be used for equipment manufactured prior to January 1, 2023.

## Table C403.3.2(2)
TABLE C403.3.2(2)
MINIMUM EFFICIENCY REQUIREMENTS: ELECTRICALLY OPERATED AIR-COOLED UNITARY HEAT PUMPS
EQUIPMENT TYPE | SIZE CATEGORY | HEATING SECTION TYPE | SUBCATEGORY OR RATING CONDITION | MINIMUM EFFICIENCY | TEST PROCEDURE a
Air cooled (cooling mode) | < 66,000 Btu/h | All | Split System b
14.0 SEERd
14.3 SEER2
before 1/1/2023
AHRI 210/240-2017
|  |  | Single Package b | 14.0 SEERd
|  |  |  | 13.4 SEER2 | after 1/1/2023
Space constrained, air cooled (cooling mode) |  30,000 Btu/h | All | Split System and Single Package b | 12.0 SEERd
|  |  |  | 11.7 SEER2 | AHRI 210/240-2023
Single-duct high-velocity, air cooled (cooling mode) | < 65,000 Btu/h | All | Split System b | 12.0 SEERd
12.0 SEER2
Air cooled (cooling mode) |  65,000 Btu/h and | Electric Resistance | Split System and Single Package | 11.0 EERd | AHRI 340/360
| < 135,000 Btu/h | (or None) |  | 12.2 IEERd
14.1 IEER
|  | All other | Split System and Single Package | 10.8 EERd
12.0 IEERd
13.9 IEER
|  135,000 Btu/h and | Electric Resistance | Split System and Single Package | 10.6 EERd
| < 240,000 Btu/h | (or None) |  | 11.6 IEERd
13.5 IEER
|  | All other | Split System and Single Package | 10.4 EERd
11.4 IEERd
13.3 IEER
|  240,000 Btu/h | Electric Resistance | Split System and Single Package | 9.5 EERd
|  | (or None) |  | 10.6 IEERd
12.5 IEER
|  | All other | Split System and Single Package | 9.3 EERd
10.4 IEERd
12.3 IEER
Air cooled (heating mode) | < 65,000 Btu/h | All | Split System b | 8.2 HSPF d | AHRI 210/240-2017
7.5 HSPF2
before 1/1/2023
AHRI 210/240-2023
after 1/1/202
|  | All | Single Package b | 8.0 HSPF d
6.7 HSPF2
Space constrained, air cooled (heating mode) |  30,000 Btu/h | All | Split System and Single Package b | 7.4 HSPF d
6.3 HSPF2
Small-duct high velocity, air cooled (heating mode) | < 65,000 Btu/h | All | Split System b | 7.4 HSPF d
6.1 HSPF2
Air cooled (heating mode) |  65,000 Btu/h and | All | 47ºF db/43ºF wb | 3.30 COPH d | AHRI 340/360
| < 135,000 Btu/h (cooling capacity) |  | outdoor air | 3.40 COPH
|  |  | 17ºF db/15ºF wb outdoor air | 2.25 COP H
|  135,000 Btu/h and | All | 47ºF db/43ºF wboutdoor air | 3.20 COPH d
| < 240,000 Btu/h (cooling capacity) |  |  | 3.30 COPH
|  |  | 17ºF db/15ºF wb outdoor air | 2.05 COPH
|  240,000 Btu/h (cooling capacity) | All | 47ºF db/43ºF wb | 3.20 COPH
outdoor air
|  |  | 17ºF db/15ºF wb | 2.05 COPH
outdoor air
For SI: 1 British thermal unit per hour = 0.2931 W, °C = [(°F) – 32]/1.8.
a | Chapter 6 contains a complete specification of the referenced test procedure, including the reference year version of the test procedure.
b | Single-phase, US air-cooled heat pumps less than 65,000 Btu/h are regulated as consumer products by the US Department of Energy Code of Federal Regulations DOE 10 CFR 430. SEER, SEER2 and HSPF values for single-phase products are set by the US Department of Energy.
c | This table is a replica of ASHRAE 90.1 Table 6.8.1-2 Electrically Operated Air-cooled Unitary Heat Pumps-Minimum Efficiency Requirements less the values for equipment for applications outside the US.
d | This efficiency value shall be used for equipment manufactured prior to January 1, 2023.

## Table C403.3.2(3)
TABLE C403.3.2(3)
WATER CHILLING PACKAGES – EFFICIENCY REQUIREMENTS a, b, e, f
EQUIPMENT TYPE | SIZE CATEGORY | UNITS | PATH A | PATH B | TEST PROCEDURE c
Air-cooled chillers | < 150 Tons | EER (Btu/Wh) |  10.100 FL |  9.700 FL | AHRI 550/ 590
|  |  |  13.700 IPLV.IP |  15.800 IPLV.IP
|  150 Tons |  |  10.100 FL |  9.700 FL
|  |  |  14.000 IPLV.IP |  16.100 IPLV.IP
Air cooled without condenser, electrically operated | All capacities | EER (Btu/Wh) | Air-cooled chillers without condenser shall be rated with matching condensers and comply with air-cooled chiller efficiency requirements.
Water cooled, electrically operated positive displacement | < 75 Tons | kW/ton |  0.750 FL |  0.780 FL
|  |  |  0.600 IPLV.IP |  0.500 IPLV.IP
|  75 tons and < 150 tons |  |  0.720 FL |  0.750 FL
|  |  |  0.560 IPLV.IP |  0.490 IPLV.IP
|  150 tons and < 300 tons |  |  0.660 FL |  0.680 FL
|  |  |  0.540 IPLV.IP |  0.440 IPLV.IP
|  300 tons and < 600 tons |  |  0.610 FL |  0.625 FL
|  |  |  0.520 IPLV.IP |  0.410 IPLV.IP
|  600 tons |  |  0.560 FL |  0.585 FL
|  |  |  0.500 IPLV.IP |  0.380 IPLV.IP
Water cooled, electrically operated centrifugal | < 150 Tons | kW/ton |  0.610 FL |  0.695 FL
|  |  |  0.550 IPLV.IP |  0.440 IPLV.IP
|  150 tons and < 300 tons |  |  0.610 FL |  0.635 FL
|  |  |  0.550 IPLV.IP |  0.400 IPLV.IP
|  300 tons and < 400 tons |  |  0.560 FL |  0.595 FL
|  |  |  0.520 IPLV.IP |  0.390 IPLV.IP
|  400 tons and < 600 tons |  |  0.560 FL |  0.585 FL
|  |  |  0.500 IPLV.IP |  0.380 IPLV.IP
|  600 Tons |  |  0.560 FL |  0.585 FL
|  |  |  0.500 IPLV.IP |  0.380 IPLV.IP
Air cooled, absorption, single effect | All capacities | COP (W/W) |  0.600 FL | NA d | AHRI 560
Water cooled absorption, single effect | All capacities | COP (W/W) |  0.700 FL | NA d
Absorption, double effect, indirect fired | All capacities | COP (W/W) |  1.000 FL | NA d
 0.150 IPLV.IP
Absorption double effect direct fired | All capacities | COP (W/W) |  1.000 FL | NA d
 1.000 IPLV
a | Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure.
b | The requirements for centrifugal chiller shall be adjusted for nonstandard rating conditions in accordance with Section C403.3.2.1 and are only applicable for the range of conditions listed there. The requirements for air-cooled, water-cooled positive displacement and absorption chillers are at standard rating conditions defined in the reference test procedure.
c | Both the full-load and IPLV.IP requirements shall be met or exceeded to comply with this standard. Where there is a Path B, compliance can be with either Path A or Path B for any application.
d | NA means the requirements are not applicable for Path B and only Path A can be used for compliance.
e | FL is the full-load performance requirements and IPLV.IP the part-load performance requirements.
f | This table is a replica of ASHRAE 90.1 Table 6.8.1-3 Water-Chilling Packages- Minimum Efficiency Requirements less the values for equipment for applications outside the US.

## Table C403.3.2(4)
TABLE C403.3.2(4)
MINIMUM EFFICIENCY REQUIREMENTS: ELECTRICALLY OPERATED PACKAGED TERMINAL AIR CONDITIONERS, PACKAGED TERMINAL HEAT PUMPS, SINGLE-PACKAGE VERTICAL AIR CONDITIONERS, SINGLE PACKAGE VERTICAL HEAT PUMPS, ROOM AIR CONDITIONERS AND ROOM AIR-CONDITIONER HEAT PUMPS e
EQUIPMENT TYPE | SIZE CATEGORY (INPUT) | SUBCATEGORY OR RATING CONDITION | MINIMUM EFFICIENCY d | TEST PROCEDURE a
PTAC (cooling mode) | < 7,000 Btu/h | 95°F db/ 75°F wb outdoor air c | 11.9 EER | AHRI 310/380
standard size
| > 7,000 Btu/h and |  | 14.0 – (0.300 × Cap/1000) EER d
< 15,000 Btu/h
| > 15,000 Btu/h |  | 9.5 EER
PTAC (cooling mode) | < 7,000 Btu/h | 95°F db / 75°F wb outdoor air c | 9.4 EER
nonstandard size a
| > 7,000 Btu/h and |  | 10.9 – (0.213 × Cap/1000) EER d
< 15,000 Btu/h
| > 15,000 Btu/h |  | 7.7 EER
PTHP (cooling mode) | < 7,000 Btu/h | 95°F db / 75°F wb outdoor air c | 11.9 EER
standard size
| > 7,000 Btu/h and |  | 14.0 – (0.300 × Cap/1000) EER d
< 15,000 Btu/h
| > 15,000 Btu/h |  | 9.5 EER
PTHP (cooling mode) | < 7,000 Btu/h | 95°F db / 75°F wb outdoor air c | 9.3 EER
nonstandard size b
| > 7,000 Btu/h and |  | 10.8 – (0.213 × Cap/1000) EER d
< 15,000 Btu/h
| > 15,000 Btu/h |  | 7.6 EER
PTHP (heating mode) standard size | < 7,000 Btu/h | 95°F db / 75°F wb outdoor air c | 3.3 COPH
| > 7,000 Btu/h and |  | 3.7 – (0.052 × Cap/1000) COPH d
< 15,000 Btu/h
| > 15,000 Btu/h |  | 2.90 COPH
PTHP (heating mode) | < 7,000 Btu/h | 95°F db / 75°F wb outdoor air c | 2.7 COPH
nonstandard size b
| > 7,000 Btu/h and |  | 2.9 – (0.026 × Cap/1000) COP H d
< 15,000 Btu/h
| > 15,000 Btu/h |  | 2.5 COPH
SPVAC (cooling mode) single and three phase | < 65,000 Btu/h | 95°F db/ 75°F wb outdoor air | 11.0 EER | AHRI 390
|  65,000 Btu/h and | 95°F db/ 75°F wb outdoor air | 10.0 EER
≤ 135,000 Btu/h
|  135,000 Btu/h and | 95°F db/ 75°F wb outdoor air | 10.0 EER
≤ 240,000 Btu/h
SPVHP (cooling mode) | < 65,000 Btu/h | 95°F db/ 75°F wb outdoor air | 11 EER
|  65,000 Btu/h and | 95°F db/ 75°F wb outdoor air | 10.0 EER
≤ 135,000 Btu/h
|  135,000 Btu/h and | 95°F db/ 75°F wb outdoor air | 10.1 EER
< 240,000 Btu/h
SPVHP (heating mode) | < 65,000 Btu/h | 47°F db/ 43°F wb outdoor air | 3.3 COP H | AHRI 390
|  65,000 Btu/h and | 47°F db/ 43°F wb outdoor air | 3.0 COP H
< 135,000 Btu/h
|  135,000 Btu/h and | 47°F db/ 75°F wb outdoor air | 3.0 COP H
< 240,000 Btu/h
Room air conditioners, without louvered sides | < 6,000 Btu/h | — | 10.0 CEER | ANSI/ AHAM RAC-1
|  6,000 Btu/h and | — | 10.0 CEER
< 8,000 Btu/h
|  8,000 Btu/h and | — | 9.6 CEER
< 11,000 Btu/h
|  11,000 Btu/h and | — | 9.5 CEER
< 14,000 Btu/h
|  14,000 Btu/h and | — | 9.3 CEER
< 20,000 Btu/h
|  20,000 Btu/h | — | 9.4 CEER
For SI: 1 British thermal unit per hour = 0.2931 W, °C = [(°F) – 32]/1.8, wb = wet bulb, db = dry bulb. “Cap” = The rated cooling capacity of the project in Btu/h. Where the unit’s capacity is less than 7000 Btu/h, use 7000 Btu/h in the calculation. Where the unit’s capacity is greater than 15,000 Btu/h, use 15,000 Btu/h in the calculations.
a | Chapter 6 contains a complete specification of the referenced test procedure, including the referenced year version of the test procedure.
b | Nonstandard size units must be factory labeled as follows: “MANUFACTURED FOR NONSTANDARD SIZE APPLICATIONS ONLY; NOT TO BE INSTALLED IN NEW STANDARD PROJECTS.” Nonstandard size efficiencies apply only to units being installed in existing sleeves having an external wall opening of less than 16 inches (406 mm) high or less than 42 inches (1067 mm) wide and having a cross-sectional area less than 670 square inches (0.43 m2 ).
c | The cooling-mode wet bulb temperature requirements only applies for units that reject condensate to the condenser coil.
d | “Cap” in EER and COPH equations for PTACs and PTHPs means cooling capacity in Btu/h at 95°F outdoor dry-bulb temperature.
e | This table is a replica of ASHRAE 90.1 Table 6.8.1-4 Electrically Operated Packaged Terminal Air Conditioners, Packaged Terminal Heat Pumps, Single- Package Vertical Air Conditioners, Single-Package Vertical Heat Pumps, Room Air Conditioners, and Room Air-Conditioner Heat Pumps—Minimum Efficiency Requirements less the values for equipment for applications outside the US.

## Table C403.3.2(5)
TABLE C403.3.2(5)
WARM-AIR FURNACES AND COMBINATION WARM-AIR FURNACES/AIR-CONDITIONING UNITS, WARM-AIR DUCT FURNACES AND UNIT HEATERS, MINIMUM EFFICIENCY REQUIREMENTS g
EQUIPMENT TYPE | SIZE CATEGORY (INPUT) | SUBCATEGORY OR RATING CONDITION | MINIMUM EFFICIENCY | TEST PROCEDURE a
Warm-air furnaces, gas fired | < 225,000 Btu/h | Maximum capacity c | before 1/1/2023 | Section 2.39, Thermal Efficiency, ANSI Z21.47
80% Et b d
After 1/1/2023
81% Et b d
Warm-air furnaces, oil fired | < 225,000 Btu/h | Maximum capacity c | before 1/1/2023 | Section 42, Combustion UL 727
80% Et
After 1/1/2023
82% Et d
Warm-air duct furnaces, gas fired | All capacities | Maximum capacity c | 80%Ec e | Section 2.10, Efficiency ANSI Z83.8
Warm-air unit heaters, gas fired | All capacities | Maximum capacity c | 80%Ec e, f
Warm-air unit heaters, oil fired | All capacities | Maximum capacity c | 80%Ec e, f | Section 40, Combustion, UL 731
For SI: 1 British thermal unit per hour = 0.2931 W.
a | Chapter 6 contains a complete specification of the referenced test procedure, including the referenced year version of the test procedure.
b | Combination units (i.e., furnaces contained within the same cabinet as an air conditioner) not covered by DOE 10 CFR 430 (i.e., three-phase power or with cooling capacity greater than or equal to 65,000 Btu/h) may comply with either rating. All other units greater than 225,000 Btu/h sold in the US must meet the AFUE standards for consumer products and test using USDOE’s AFUE test procedure at DOE 10 CFR 430, Subpart B, Appendix N.
c | Compliance of multiple firing rate units shall be at the maximum firing rate.
d | Et = Thermal efficiency. Units must also include an interrupted or intermittent ignition device (IID), have jacket losses not exceeding 0.75 percent of the input rating, and have either power venting or a flue damper. A vent damper is an acceptable alternative to a flue damper for those furnaces where combustion air is drawn from the conditioned space.
e | Ec = Combustion efficiency (100% less flue losses). See test procedure for detailed discussion.
f | Units must also include an interrupted or intermittent ignition device (IID) and have either power venting or an automatic flue damper.
g | This table is a replica of ASHRAE 90.1 Table 6.8.1-5 Warm-Air Furnaces and Combination Warm-Air Furnaces/Air-Conditioning Units, Warm-Air Duct Furnaces, and Unit Heaters—Minimum Efficiency Requirements less the values for equipment for applications outside the US.

## Table C403.3.2(6)
TABLE C403.3.2(6)
MINIMUM EFFICIENCY REQUIREMENTS: GAS- AND OIL-FIRED BOILERS i
EQUIPMENT TYPE b | SUBCATEGORY OR RATING CONDITION | SIZE CATEGORY (INPUT) | MINIMUM EFFICIENCY | EFFICIENCY AS OF 3/2/2022 | TEST PROCEDURE a
Boilers, hot water | Gas-fired |  300,000 Btu/h and | 80% Et d | 80% Et d | DOE 10 CFR Part 431.86
 2,500,000 Btu/h e
|  | > 2,500,000 Btu/h b | 82% Ec c | 82% Ec c
| Oil-fired f |  300,000 Btu/h and | 82% Et d | 82% Et d
 2,500,000 Btu/h b
|  | > 2,500,000 Btu/ha | 84% Ec c | 84% Ec c
Boilers, steam | Gas-fired- all, except natural draft |  300,000 Btu/h and | 79% Et d | 79% Et d
 2,500,000 Btu/h b
|  | > 2,500,000 Btu/ha | 79% Et d | 79% Et d
| Gas-fired-natural draft |  300,000 Btu/h and | 77% Et d | 79% Et d
 2,500,000 Btu/h b
|  | > 2,500,000 Btu/ha | 77% Et d | 79% Et d
| Oil-fired f |  300,000 Btu/h and | 81% Et d | 81% Et d
 2,500,000 Btu/h b
|  | > 2,500,000 Btu/ha | 81% Et d | 81% Et d
For SI: 1 British thermal unit per hour = 0.2931 W.
a | Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure.
b | These requirements apply to boilers with rated input of 8,000,000 Btu/h or less that are not packaged boilers and to all packaged boilers. Minimum efficiency requirements for boilers cover all capacities of packaged boilers.
c | Ec = Combustion efficiency (100 percent less flue losses).
d | Et = Thermal efficiency.
e | Maximum capacity – minimum and maximum ratings as provided for and allowed by the unit’s controls.
f | Includes oil-fired (residual).
g | Boilers shall not be equipped with a constant-burning pilot light.
h | A boiler not equipped with a tankless domestic water heating coil shall be equipped with an automatic means for adjusting the temperature of the water such that an incremental change in inferred heat load produces a corresponding incremental change in the temperature of the water supplied.
i | This table is a replica of ASHRAE 90.1 Table 6.8.1-6 Gas- and Oil-Fired Boilers—Minimum Efficiency Requirements less the values for equipment for applications outside the US.

## Table C403.3.2(7)
TABLE C403.3.2(7)
MINIMUM EFFICIENCY REQUIREMENTS: HEAT REJECTION EQUIPMENT i
EQUIPMENT TYPE | TOTAL SYSTEM HEAT REJECTION CAPACITY AT RATED CONDITIONS | SUBCATEGORY OR RATING CONDITION h | PERFORMANCE REQUIRED b, c, d, f, g | TEST PROCEDURE a, e
Propeller or axial fan open-circuit cooling towers | All | 95°F entering water |  60 gpm/hp | CTI ATC-105 and CTI STD-201 RS
85°F leaving water
75°F entering wb
Centrifugal fan open-circuit cooling towers | All | 95°F entering water |  20.0 gpm/hp | CTI ATC-105 and CTI STD-201 RS
85°F leaving water
75°F entering wb
Propeller or axial fan closed-circuit cooling towers | All | 102°F entering water |  16.1 gpm/hp | CTI ATC-105S and CTI STD-201 RS
90°F leaving water
75°F entering wb
Centrifugal fan closed- circuit cooling towers | All | 102°F entering water |  7.0 gpm/hp | CTI ATC-105S and CTI STD-201 RS
90°F leaving water
75°F entering wb
Propeller or axial fan dry coolers (air-cooled fluid coolers) | All | 115°F entering water | > 4.5 gpm/hp | CTI ATC-105DS
105°F leaving water
95°F entering wb
Propeller or axial fan evaporative condensers | All | R-448A test fluid |  160,000 Btu/h  hp | CTI ATC-106
165°F entering gas temperature
105°F condensing temperature
75°F entering wb
Propeller or axial fan evaporative condensers | All | R-448A Test Fluid |  134,000 Btu/h  hp | CTI ATC-106
140°F entering gas temperature 96.3°F condensing temperature 75°F entering wb
Centrifugal fan evaporative condensers | All | R-448A Test Fluid |  137,000 Btu/h  hp | CTI ATC-106
165°F entering gas temperature 105°F condensing temperature 75°F entering wb
Centrifugal fan evaporative condensers | All | Ammonia Test Fluid | 110,000 Btu/h  hp | CTI ATC-106
140°F entering gas temperature
96.3°F condensing temperature 75°F entering wb
Air-cooled condensers | All | 125°F Condensing Temperature |  176,000 Btu/h  hp | AHRI 460
190°F Entering Gas Temperature 15°F subcooling
95°F entering db
For SI: °C = [(°F) – 32]/1.8, L/s • kW = (gpm/hp)/(11.83), COP = (Btu/h • hp)/(2550.7) db = dry bulb temperature, °F, wb = wet bulb temperature, °F
a | Chapter 6 contains a complete specification of the referenced test procedure, including the referenced year version of the test procedure..
b | For purposes of this table, open circuit cooling tower performance is defined as the water flow rating of the tower at the thermal rating condition listed in the table, divided by the fan motor nameplate power.
c | For purposes of this table, closed-circuit cooling tower performance is defined as the water flow rating of the tower at the thermal rating condition listed in the table , divided by the sum of the fan motor nameplate power and the spray pump motor nameplate power.
d | For purposes of this table, dry-cooler performance is defined as the process water-flow rating of the unit at the thermal rating condition listed in the table divided by the total fan motor nameplate power of the unit, and air-cooled condenser performance is defined as the heat rejected form the refrigerant divided by the total fan motor nameplate power of the unit.
e | The efficiencies and test procedures for both open- and closed-circuit cooling towers are not applicable to hybrid cooling towers that contain a combination of separate wet and dry heat exchange sections. The certification requirements do not apply to field-erected cooling towers.
f | All cooling towers shall comply with the minimum efficiency listed in the table for that specific type of tower with the capacity effect of any project-specific accessories or options included in the capacity of the cooling tower
g | For purposes of this table, evaporative condenser performance is defined as the heat rejected at the specified rating condition in the table divided by the sum of the fan motor nameplate power and the integral spray pump nameplate power
h | Requirements for evaporative condensers are listed with ammonia (R-717) and R-448A as test fluids in the table. Evaporative condensers intended for use with halocarbon refrigerants other than R-448A shall meet the minimum efficiency requirements listed in this table with R-448A as the test fluid. For Ammonia, the condensing temperature is defined as the saturation temperature corresponding to the refrigerant pressure at the condenser entrance. For R-448A, which is a zeotropic refrigerant, the condensing temperature is defined as the arithmetic average of the dew point and the bubble point temperatures corresponding to the refrigerant pressure at the condenser entrance.
i | This table is a replica of ASHRAE 90.1 Table 6.8.1-7 Performance Requirements for Heat Rejection Equipment—Minimum Efficiency Requirements.

## Table C403.3.2(8)
TABLE C403.3.2(8)
ELECTRICALLY OPERATED VARIABLE-REFRIGERANT-FLOW AIR CONDITIONERS-MINIMUM EFFICIENCY REQUIREMENTS b
EQUIPMENT TYPE | SIZE CATEGORY | HEATING SECTION TYPE | SUBCATEGORY OR RATING CONDITION | MINIMUM EFFICIENCY | TEST PROCEDURE a
VRF air conditioners, air cooled | < 65,000 Btu/h | All | VRF multisplit system | 13.0 SEER | AHRI 1230
| > 65,000 Btu/h and < 135,000 Btu/h | Electric resistance | VRF multisplit system | 11.2 EER
|  | (or none) |  | 13.1 IEER
15.5 IEER
| > 135,000 Btu/h and < 240,000 Btu/h | Electric resistance | VRF multisplit system | 11.0 EER
|  | (or none) |  | 12.9 IEER
14.9 IEER
| > 240,000 Btu/h | Electric resistance | VRF multisplit system | 10.0 EER
|  | (or none) |  | 11.6 IEER
13.9 IEER
For SI: 1 British thermal unit per hour = 0.2931 W.
a | Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure.
b | This table is a replica of ASHRAE 90.1 Table 6.8.1-8 Electrically Operated Variable-Refrigerant-Flow Air Conditioners—Minimum Efficiency Requirements.

## Table C403.3.2(9)
TABLE C403.3.2(9)
ELECTRICALLY OPERATED VARIABLE-REFRIGERANT-FLOW AND APPLIED HEAT PUMPS-MINIMUM EFFICIENCY REQUIREMENTS b
EQUIPMENT TYPE | SIZE CATEGORY | HEATING SECTION TYPE | SUBCATEGORY OR RATING CONDITION | MINIMUM EFFICIENCY | TEST PROCEDURE a
VRF air cooled (cooling mode) | < 65,000 Btu/h | All | VRF multisplit system | 13.0 SEER | AHRI 1230
| > 65,000 Btu/h and < 135,000 Btu/h | Electric resistance (or none) |  | 11.0 EER
12.9 IEER
14.6 IEER
|  |  | VRF multisplit system with heat recovery | 10.8 EER
12.7 IEER
14.4 IEER
| > 135,000 Btu/h and < 240,000 Btu/h |  | VRF multisplit system | 10.6 EER
12.3 IEER
13.9 IEER
|  |  | VRF multisplit system with heat recovery | 10.4 EER
12.1 IEER
13.7 IEER
| > 240,000 Btu/h |  | VRF multisplit system | 9.5 EER
11.0 IEER
12.7 IEER
|  |  | VRF multisplit system with heat recovery | 9.3 EER
10.8 IEER
12.5 IEER
VRF water source (cooling mode) | < 65,000 Btu/h | All | VRF multisplit systems 86oF entering water | 12.0 EER | AHRI 1230
16.0 IEER
|  |  | VRF multisplit systems with heat recovery 86oF entering water | 11.8 EER
15.8 IEER
| > 65,000 Btu/h and < 135,000 Btu/h |  | VRF multisplit system 86oF entering water | 12.0 EER
16.0 IEER
|  |  | VRF multisplit system with heat recovery 86oF entering water | 11.8 EER
15.8 IEER
| > 135,000 Btu/h and < 240,000 Btu/h |  | VRF multisplit system 86oF entering water | 10.0 EER
14.0 IEER
|  |  | VRF multisplit system with heat recovery 86oF entering water | 9.8 EER
13.8 IEER
| > 240,000 Btu/h |  | VRF multisplit system 86oF entering water | 10.0 EER
12.0 IEER
|  |  | VRF multisplit system with heat recovery 86oF entering water | 9.8 EER
11.8 IEER
VRF groundwater source (cooling mode) | < 135,000 Btu/h | All | VRF multisplit system 59oF entering water | 16.2 EER | AHRI 1230
|  |  | VRF multisplit system with heat recovery 59oF entering water | 16.0 EER
| > 135,000 Btu/h |  | VRF multisplit system 59oF entering water | 13.8 EER
|  |  | VRF multisplit system with heat recovery 59oF entering water | 13.6 EER
VRF ground source (cooling mode) | < 135,000 Btu/h | All | VRF multisplit system 77oF entering water | 13.4 EER | AHRI 1230
|  |  | VRF multisplit system with heat recovery 77oF entering water | 13.2 EER
| > 135,000 Btu/h |  | VRF multisplit system 77oF entering water | 11.0 EER
|  |  | VRF multisplit system with heat recovery 77oF entering water | 10.8 EER
VRF air cooled (heating mode) | < 65,000 Btu/h (cooling capacity) |  | VRF multisplit system | 7.7 HSPF | AHRI 1230
| > 65,000 Btu/h and < 135,000 Btu/h (cooling capacity) |  | VRF multisplit system 47oF db/ 43 oF wb outdoor air | 3.3 COPH
|  |  | 17oF db/ 15 oF wb outdoor air | 2.25 COPH
| > 135,000 Btu/h (cooling capacity) |  | VRF multisplit system 47oF db/ 43 oF wb outdoor air | 3.2 COPH
|  |  | 17oF db/ 15 oF wb outdoor air | 2.05 COPH
VRF water source (heating mode) | < 65,000 Btu/h (cooling capacity) |  | VRF multisplit system 68oF entering water | 4.2 COPH | AHRI 1230
4.3 COPH
| > 65,000 Btu/h and |  | VRF multisplit system 68oF entering water | 4.2 COPH
| < 135,000 Btu/h (cooling capacity) |  |  | 4.3 COPH
| > 135,000 Btu/h and |  | VRF multisplit system 68oF entering water | 3.9 COPH
| < 240,000 Btu/h (cooling capacity) |  |  | 4.0 COPH
| > 240,000 Btu/h |  | VRF multisplit system 68oF entering water | 3.9 COPH
VRF groundwater source (heating mode) | < 135,000 Btu/h (cooling capacity) |  | VRF multisplit system 50oF entering water | 3.6 COPH | AHRI 1230
| > 135,000 Btu/h (cooling capacity) |  | VRF multisplit system 50oF entering water | 3.3 COPH
VRF ground source (heating mode) | < 135,000 Btu/h (cooling capacity) |  | VRF multisplit system 32oF entering water | 3.1 COPH | AHRI 1230
| > 135,000 Btu/h (cooling capacity) |  | VRF multisplit system 32oF entering water | 2.8 COPH
For SI: oC = [(oF)-32]/1.8, 1 British thermal unit per hour = 0.2931 W, db = dry bulb temperature, wb = wet bulb temperature.
a | Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure.
b | This table is a replica of ASHRAE 90.1 Table 6.8.1-9 Electrically Operated Variable-Refrigerant-Flow and Applied Heat Pumps—Minimum Efficiency Requirements.

## Table C403.3.2(10)
TABLE C403.3.2(10)
FLOOR-MOUNTED AIR CONDITIONERS AND CONDENSING UNITS SERVING COMPUTER ROOMS-MINIMUM EFFICIENCY REQUIREMENTS b
EQUIPMENT TYPE | STANDARD MODEL | NET SENSIBLE COOLING CAPACITY | MINIMUM NET SENSIBLE COP | RATING CONDITIONS RETURN AIR (dry bulb/dew point) | TEST PROCEDURE a
Air cooled | Downflow | < 80,000 Btu/h | 2.70 | 85oF/52oF (Class 2) | AHRI 1360
|  | > 80,000 Btu/h and < 295,000 Btu/h | 2.58
|  | > 295,000 Btu/h | 2.36
| Upflow-ducted | < 80,000 Btu/h | 2.67
|  | > 80,000 Btu/h and < 295,000 Btu/h | 2.55
|  | > 295,000 Btu/h | 2.33
| Upflow-nonducted | < 65,000 Btu/h | 2.16 | 75oF/52oF (Class 1)
|  | > 65,000 Btu/h and < 240,000 Btu/h | 2.04 | 75oF/52oF (Class 1)
|  | > 240,000 Btu/h | 1.89
| Horizontal | < 65,000 Btu/h | 2.65 | 95oF/52oF (Class 3)
|  | > 65,000 Btu/h and < 240,000 Btu/h | 2.55
|  | > 240,000 Btu/h | 2.47
Air cooled with fluid economizer | Downflow | < 80,000 Btu/h | 2.70 | 85oF/52oF (Class 1)
|  | > 80,000 Btu/h and < 295,000 Btu/h | 2.58
|  | > 295,000 Btu/h | 2.36
| Upflow-ducted | < 80,000 Btu/h | 2.67
|  | > 80,000 Btu/h and < 295,000 Btu/h | 2.55
|  | > 295,000 Btu/h | 2.33
| Upflow-nonducted | < 65,000 Btu/h | 2.09 | 75oF/52oF (Class 1)
|  | > 65,000 Btu/h and < 240,000 Btu/h | 1.99
|  | > 240,000 Btu/h | 1.81
| Horizontal | < 65,000 Btu/h | 2.65 | 95oF/52oF (Class 3)
|  | > 65,000 Btu/h and < 240,000 Btu/h | 2.55
|  | > 240,000 Btu/h | 2.47
Water cooled economizer | Downflow | < 80,000 Btu/h | 2.82 | 85oF/52oF (Class 1)
|  | > 80,000 Btu/h and < 295,000 Btu/h | 2.73
|  | > 295,000 Btu/h | 2.67
| Upflow- ducted | < 80,000 Btu/h | 2.79
|  | > 80,000 Btu/h and < 295,000 Btu/h | 2.70
|  | > 295,000 Btu/h | 2.64
| Upflow-nonducted | < 65,000 Btu/h | 2.43 | 75oF/52oF (Class 1)
|  | > 65,000 Btu/h and < 240,000 Btu/h | 2.32
|  | > 240,000 Btu/h | 2.20
| Horizontal | < 65,000 Btu/h | 2.79 | 95oF/52oF (Class 3)
|  | > 65,000 Btu/h and < 240,000 Btu/h | 2.68
|  | > 240,000 Btu/h | 2.60
Water cooled with fluid Water cooled economizer (cont.) | Downflow | < 80,000 Btu/h | 2.77 | 85oF/52oF (Class 1)
|  | > 80,000 Btu/h and < 295,000 Btu/h | 2.68
|  | > 295,000 Btu/h | 2.61
| Upflow-ducted | < 80,000 Btu/h | 2.74
|  | > 80,000 Btu/h and < 295,000 Btu/h | 2.65
|  | > 295,000 Btu/h | 2.58
| Upflow-nonducted | < 65,000 Btu/h | 2.35 | 75oF/52oF (Class 1)
|  | > 65,000 Btu/h and < 240,000 Btu/h | 2.24
|  | > 240,000 Btu/h | 2.12
| Horizontal | < 65,000 Btu/h | 2.71 | 95oF/52oF (Class 3)
|  | > 65,000 Btu/h and < 240,000 Btu/h | 2.60
|  | > 240,000 Btu/h | 2.54
Glycol cooled | Downflow | < 80,000 Btu/h | 2.56 | 85oF/52oF (Class 1)
|  | > 80,000 Btu/h and < 295,000 Btu/h | 2.24
|  | > 295,000 Btu/h | 2.21
| Upflow-ducted | < 80,000 Btu/h | 2.53 | 85oF/52oF (Class 1)
|  | > 80,000 Btu/h and < 295,000 Btu/h | 2.21
|  | > 295,000 Btu/h | 2.18
| Upflow-nonducted | < 65,000 Btu/h | 2.08 | 75oF/52oF (Class 1)
|  | > 65,000 Btu/h and < 240,000 Btu/h | 1.90
|  | > 240,000 Btu/h | 1.81
| Horizontal | < 65,000 Btu/h | 2.48 | 95oF/52oF (Class 3)
|  | > 65,000 Btu/h and < 240,000 Btu/h | 2.18
|  | > 240,000 Btu/h | 2.18
Glycol cooled with fluid economizer | Downflow | < 80,000 Btu/h | 2.51 | 85oF/52oF (Class 1)
|  | > 80,000 Btu/h and < 295,000 Btu/h | 2.19
|  | > 295,000 Btu/h | 2.15
| Upflow-ducted | < 80,000 Btu/h | 2.48
|  | > 80,000 Btu/h and < 295,000 Btu/h | 2.16
|  | > 295,000 Btu/h | 2.12
| Upflow-nonducted | < 65,000 Btu/h | 2.00 | 75oF/52oF (Class 1)
|  | > 65,000 Btu/h and < 240,000 Btu/h | 1.82
|  | > 240,000 Btu/h | 1.73
| Horizontal | < 65,000 Btu/h | 2.44 | 95oF/52oF (Class 3)
|  | > 65,000 Btu/h and < 240,000 Btu/h | 2.10
|  | > 240,000 Btu/h | 2.10
For SI: 1 British thermal unit per hour = 0.2931 W, oC = [(oF)-32]/1.8, COP = (Btu/h x hp)/(2,550.7).
a | Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure.
b | This table is a replica of ASHRAE 90.1 Table 6.8.1-10 Floor-Mounted Air Conditioners and Condensing Units Serving Computer Rooms—Minimum Efficiency Requirements.

## Table C403.3.2(11)
TABLE C403.3.2(11)
VAPOR-COMPRESSION-BASED INDOOR POOL DEHUMIDIFIERS-MINIMUM EFFICIENCY REQUIREMENTS b
EQUIPMENT TYPE | SUBCATEGORY OR RATING CONDITION | MINIMUM EFFICIENCY | TEST PROCEDURE a
Single package indoor (with or without economizer) | Rating Conditions: A or C | 3.5 MRE | AHRI 910
Single package indoor water cooled (with or without economizer) | Rating Conditions: A, B or C | 3.5 MRE
Single package indoor air cooled (with or without economizer) | Rating Conditions: A, B or C | 3.5 MRE
Split system indoor air cooled (with or without economizer) | Rating Conditions: A, B or C | 3.5 MRE
a | Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure.
b | This table is a replica of ASHRAE 90.1 Table 6.8.1-12 Vapor-Compression-Based Indoor Pool Dehumidifiers—Minimum Efficiency Requirements.

## Table C403.3.2(12)
TABLE C403.3.2(12)
ELECTRICALLY OPERATED DX-DOAS UNITS, SINGLE-PACKAGE AND REMOTE CONDENSER, WITHOUT ENERGY RECOVERY- MINIMUM EFFICIENCY REQUIREMENTS b
EQUIPMENT TYPE | SUBCATEGORY OR RATING CONDITION | MINIMUM EFFICIENCY | TEST PROCEDURE a
Air cooled and Air-source heat pumps (dehumidification mode) | - | 4.0 ISMRE | AHRI 920
Water cooled (dehumidification mode) | Cooling tower condenser water | 4.9 ISMRE
| Chilled water | 6.0 ISMRE
Air-source heat pump (heating mode) | - | 2.7 ISCOP
Water-source heat pump (dehumidification mode) | Ground source, closed loop | 4.8 ISMRE
| Ground-water source | 5.0 ISMRE
| Water source | 4.0 ISMRE
Water-source heat pump (heating mode) | Ground source, closed loop | 2.0 ISCOP | AHRI 920
| Ground-water source | 3.2 ISCOP
| Water source | 3.5 ISCOP
a | Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure.
b | This table is a replica of ASHRAE 90.1 Table 6.8.1-13 Electrically Operated DX-DOAS Units, Single-Package and Remote Condenser, without Energy Recovery—Minimum Efficiency Requirements.

## Table C403.3.2(13)
TABLE C403.3.2(13)
ELECTRICALLY OPERATED DX-DOAS UNITS, SINGLE-PACKAGE AND REMOTE CONDENSER, WITH ENERGY RECOVERY- MINIMUM EFFICIENCY REQUIREMENTS b
EQUIPMENT TYPE | SUBCATEGORY OR RATING CONDITION | MINIMUM EFFICIENCY | TEST PROCEDURE a
Air cooled and Air-source heat pumps (dehumidification mode) | - | 5.2 ISMRE | AHRI 920
AHRI 920
Water cooled (dehumidification mode) | Cooling tower condenser water | 5.3 ISMRE | AHRI 920
| Chilled water | 6.6 ISMRE
Air-source heat pump (heating mode) | - | 3.3 ISCOP | AHRI 920
Water-source heat pump (dehumidification mode) | Ground source, closed loop | 5.2 ISMRE | AHRI 920
| Ground-water source | 5.8 ISMRE
| Water source | 4.8 ISMRE
Water-source heat pump (heating mode) | Ground source, closed loop | 3.8 ISCOP | AHRI 920
| Ground-water source | 4.0 ISCOP
| Water source | 4.8 ISCOP
a | Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure.
b | This table is a replica of ASHRAE 90.1 Table 6.8.1-14 Electrically Operated DX-DOAS Units, Single-Package and Remote Condenser, with Energy Recovery—Minimum Efficiency Requirements.

## Table C403.3.2(14)
TABLE C403.3.2(14)
ELECTRICALLY OPERATED WATER-SOURCE HEAT PUMPS- MINIMUM EFFICIENCY REQUIREMENTS c
EQUIPMENT TYPE | SIZE CATEGORY b | HEATING SECTION TYPE | SUBCATEGORY OR RATING CONDITION | MINIMUM EFFICIENCY | TEST PROCEDURE a
Water-to-air, water loop (cooling mode) | < 17,000 Btu/h | All | 86°F entering water | 12.2 EER | ISO 13256-1
| ≥ 17,000 Btu/h and < 65,000 Btu/h |  |  | 13.0 EER
| ≥ 65,000 Btu/h and < 135,000 Btu/h |  |  | 13.0 EER
Water-to-air, ground water (cooling mode) | < 135,000 Btu/h | All | 59°F entering water | 18.0 EER | ISO 13256-1
Brine-to-air, ground loop (cooling mode) |  |  | 77°F entering water | 14.1 EER
Water-to-water, water loop (cooling mode) |  |  | 86°F entering water | 10.6 EER | ISO 13256-2
Water-to-water, ground water (cooling mode) |  |  | 59°F entering water | 16.3 EER
Brine-to-water, ground loop (cooling mode) |  |  | 77°F entering water | 12.1 EER
Water-to-water, water loop (heating mode) | < 135,000 Btu/h (cooling capacity) | - | 68°F entering water | 4.3 COPH | ISO 13256-1
Water-to-air, ground water (heating mode) |  |  | 50°F entering water | 3.7 COPH
Brine-to-air, ground loop (heating mode) |  |  | 32°F entering water | 3.2 COPH
Water-to-water, water loop (heating mode) |  |  | 68°F entering water | 3.7 COPH
Water-to-water, ground water (heating mode) |  |  | 50°F entering water | 3.1 COPH | ISO 13256-2
Brine-to-water, ground loop (heating mode) |  |  | 32°F entering water | 2.5 COPH
For SI: 1 British thermal unit per hour = 0.2931 W, oC = [(oF)-32]/1.8.
a | Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure.
b | Single-phase, US air-cooled heat pumps less than 19 kW are regulated as consumer products by DOE 10 CFR 430. SCOPC, SCOP2C, SCOPH and SCOP2H values for single-phase products are set by the USDOE.
c | This table is a replica of ASHRAE 90.1 Table 6.8.1-15 Electrically Operated Water-Source Heat Pumps—Minimum Efficiency Requirements.

## Table C403.3.2(15)
TABLE C403.3.2(15)
HEAT-PUMP AND HEAT RECOVERY CHILLER PACKAGES- MINIMUM EFFICIENCY REQUIREMENTS g
HEATING OPERATION
EQUIPMENT TYPE | SIZE CATEGORY, tonR | COOLING-ONLY OPERATION COOLING EFFICIENCY c AIR-SOURCE EER (FL/IPLV), Btu/W × h WATER-SOURCE POWER INPUT PER CAPACITY (FL/IPLV), kW/tonR |  | HEATING SOURCE | HEAT-PUMP HEATING FULL-LOAD EFFICIENCY (COPH) b, W/W |  |  |  | EAT RECOVERY CHILLER FULL-LOAD EFFICIENCY (COPHR) c, d, W/W SIMULTANEOUS COOLING AND HEATING FULL-LOAD EFFICIENCY (COPSHC) c, W/W |  |  |  | TEST PROCEDURE A
CONDITIONS (entering/ leaving
water) OR OAT (db/wb), °F
[5 empty] | Leaving Heating Water Temperature |  |  |  | Leaving Heating Water Temperature
[5 empty] | Low | Medium | High | Boost | Low | Medium | High | Boost
|  | Path A | Path B |  | 105°F | 120°F | 140°F | 140°F | 105°F | 120°F | 140°F | 140°F
Air source | All sizes | ≥ 9.595 FL ≥ 13.02 IPLV.IP | ≥ 9.215 FL ≥ 15.01 IPLV.IP | 47 db 43 wb e | ≥ 3.290 | ≥ 2.770 | ≥ 2.310 | NA | NA | NA | NA | NA | AHRI 550/590
|  | ≥ 9.595 FL ≥ 13.30 IPLV.IP | ≥ 9.215 FL ≥ 15.30 IPLV.IP | 17 db 15 wb e | ≥ 2.230 | ≥ 1.950 | ≥ 1.630 | NA | NA | NA | NA | NA
Water-source electrically operated positive displacement | < 75 | ≤ 0.7885 FL ≤ 0.6316 IPLV.IP | ≤ 0.7875 FL ≤ 0.5145 IPLV.IP | 54/44 f | ≥ 4.640 | ≥ 3.680 | ≥ 2.680 | NA | ≥ 8.330 | ≥ 6.410 | ≥ 4.420 | NA
|  |  |  | 75/65 f | NA | NA | NA | ≥ 3.550 | NA | NA | NA | ≥ 6.150
| ≥ 75 and < 150 | ≤ 0.7579 FL ≤ 0.5895 IPLV.IP | ≤ 0.7140 FL ≤ 0.4620 IPLV.IP | 54/44 f | ≥ 4.640 | ≥ 3.680 | ≥ 2.680 | NA | ≥ 8.330 | ≥ 6.410 | ≥ 4.420 | NA
|  |  |  | 75/65 f | NA | NA | NA | ≥ 3.550 | NA | NA | NA | ≥ 6.150
| ≥ 150 and < 300 | ≤ 0.6947 FL ≤ 0.5684 IPLV.IP | ≤ 0.7140 FL ≤ 0.4620 IPLV.IP | 54/44 f | ≥ 4.640 | ≥ 3.680 | ≥ 2.680 | NA | ≥ 8.330 | ≥ 6.410 | ≥ 4.420 | NA
|  |  |  | 75/65 f | NA | NA | NA | ≥ 3.550 | NA | NA | NA | ≥ 6.150
| ≥ 300 and < 600 | ≤ 0.6421 FL ≤ 0.5474 IPLV.IP | ≤ 0.6563 FL ≤ 0.4305 IPLV.IP | 54/44 f | ≥ 4.930 | ≥ 3.960 | ≥ 2.970 | NA | ≥ 8.900 | ≥ 6.980 | ≥ 5.000 | NA
|  |  |  | 75/65 f | NA | NA | NA | ≥ 3.900 | NA | NA | NA | ≥ 6.850
| ≥ 600 | ≤ 0.5895 FL ≤ 0.5263 IPLV.IP | ≤ 0.6143 FL ≤ 0.3990 IPLV.IP | 54/44 f | ≥ 4.930 | ≥ 3.960 | ≥ 2.970 | NA | ≥ 8.900 | ≥ 6.980 | ≥ 5.000 | NA
|  |  |  | 75/65 f | NA | NA | NA | ≥ 3.900 | NA | NA | NA | ≥ 6.850
Water-source electrically operated centrifugal | < 75 | ≤ 0.6421 FL ≤ 0.5789 IPLV.IP | ≤ 0.7316 FL ≤ 0.4632 IPLV.IP | 54/44 f | ≥ 4.640 | ≥ 3.680 | ≥ 2.680 | NA | ≥ 8.330 | ≥ 6.410 | ≥ 4.420 | NA
|  |  |  | 75/65 f | NA | NA | NA | ≥ 3.550 | NA | NA | NA | ≥ 6.150
| ≥ 75 and < 150 | ≤ 0.5895 FL ≤ 0.5474 IPLV.IP | ≤ 0.6684 FL ≤ 0.4211 IPLV.IP | 54/44 f | ≥ 4.640 | ≥ 3.680 | ≥ 2.680 | NA | ≥ 8.330 | ≥ 6.410 | ≥ 4.420 | NA
|  |  |  | 75/65 f | NA | NA | NA | ≥ 3.550 | NA | NA | NA | ≥ 6.150
| ≥ 150 and < 300 | ≤ 0.5895 FL ≤ 0.5263 IPLV.IP | ≤ 0.6263 FL ≤ 0.4105 IPLV.IP | 54/44 f | ≥ 4.640 | ≥ 3.680 | ≥ 2.680 | NA | ≥ 8.330 | ≥ 6.410 | ≥ 4.420 | NA
|  |  |  | 75/65 f | NA | NA | NA | ≥ 3.550 | NA | NA | NA | ≥ 6.150
| ≥ 300 and < 600 | ≤ 0.5895 FL ≤ 0.5263 IPLV.IP | ≤ 0.6158 FL ≤ 0.4000 IPLV.IP | 54/44 f | ≥ 4.930 | ≥ 3.960 | ≥ 2.970 | NA | ≥ 8.900 | ≥ 6.980 | ≥ 5.000 | NA
|  |  |  | 75/65 f | NA | NA | NA | ≥ 3.900 | NA | NA | NA | ≥ 6.850
| ≥ 600 | ≤ 0.5895 FL ≤ 0.5263 IPLV.IP | ≤ 0.6158 FL ≤ 0.4000 IPLV.IP | 54/44 f | ≥ 4.930 | ≥ 3.960 | ≥ 2.970 | NA | ≥ 8.900 | ≥ 6.980 | ≥ 5.000 | NA
|  |  |  | 75/65f | NA | NA | NA | ≥ 3.900 | NA | NA | NA | ≥ 6.850
For SI: oC = [(oF)-32]/1.8.
a | Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure.
b | Cooling-only rating conditions are standard rating conditions defined in AHRI 550/590, Table 1.
c | Heating full-load rating conditions are at rating conditions defined in AHRI 550/590, Table 1.
d | For water-cooled heat recovery chillers that have capabilities for heat rejection to a heat recovery condenser and a tower condenser, the COPHR applies to operation at full load with 100 percent heat recovery (no tower rejection). Units that only have capabilities for partial heat recovery shall meet the requirements of Table C403.3.2(3).
e | Outdoor air entering dry-bulb (db) temperature and wet-bulb (wb) temperature.
f | Source-water entering and leaving water temperature.
g | This table is a replica of ASHRAE 90.1 Table 6.8.1-16 Heat-Pump and Heat Recovery Chiller Packages —Minimum Efficiency Requirements.

## Table C403.3.2(16)
TABLE C403.3.2(16)
CEILING-MOUNTED COMPUTER-ROOM AIR CONDITIONERS – MINIMUM EFFICIENCY REQUIREMENTS b
EQUIPMENT TYPE | STANDARD MODEL | NET SENSIBLE COOLING CAPACITY | MINIMUM NET SENSIBLE COP | RATING CONDITIONS RETURN AIR (dry bulb/ dew point) | TEST PROCEDURE a
Air cooled with free air discharge condenser | Ducted | < 29,000 Btu/h | 2.05 | 75°F/52°F (Class 1) | AHRI 1360
|  | ≥ 29,000 Btu/h and < 65,000 Btu/h | 2.02
|  | ≥ 65,000 Btu/h | 1.92
| Nonducted | < 29,000 Btu/h | 2.08
|  | ≥ 29,000 Btu/h and < 65,000 Btu/h | 2.05
|  | ≥ 65,000 Btu/h | 1.94
Air cooled with free air discharge condenser with fluid economizer | Ducted | < 29,000 Btu/h | 2.01
|  | ≥ 29,000 Btu/h and | 1.97
< 65,000 Btu/h
|  | ≥ 65,000 Btu/h | 1.87
| Nonducted | < 29,000 Btu/h | 2.04
|  | ≥ 29,000 Btu/h and < 65,000 Btu/h | 2.00
|  | ≥ 65,000 Btu/h | 1.89
Air cooled with ducted condenser | Ducted | < 29,000 Btu/h | 1.86
|  | ≥ 29,000 Btu/h and < 65,000 Btu/h | 1.83
|  | ≥ 65,000 Btu/h | 1.73
| Nonducted | < 29,000 Btu/h | 1.89
|  | ≥ 29,000 Btu/h and < 65,000 Btu/h | 1.86
|  | ≥ 65,000 Btu/h | 1.75
Air cooled with fluid economizer and ducted condenser | Ducted | < 29,000 Btu/h | 1.82
|  | ≥ 29,000 Btu/h and < 65,000 Btu/h | 1.78
|  | ≥ 65,000 Btu/h | 1.68
| Nonducted | < 29,000 Btu/h | 1.85
|  | ≥ 29,000 Btu/h and < 65,000 Btu/h | 1.81
|  | ≥ 65,000 Btu/h | 1.70
Water cooled | Ducted | < 29,000 Btu/h | 2.38
|  | ≥ 29,000 Btu/h and < 65,000 Btu/h | 2.38
|  | ≥ 65,000 Btu/h | 2.18
| Nonducted | < 29,000 Btu/h | 2.41
|  | ≥ 29,000 Btu/h and < 65,000 Btu/h | 2.31
|  | ≥ 65,000 Btu/h | 2.20
Water cooled with fluid economizer | Ducted | < 29,000 Btu/h | 2.33
|  | ≥ 29,000 Btu/h and < 65,000 Btu/h | 2.23
|  | ≥ 65,000 Btu/h | 2.13
| Nonducted | < 29,000 Btu/h | 2.36
| Nonducted | ≥ 29,000 Btu/h and < 65,000 Btu/h | 2.26
(cont.)
|  | ≥ 65,000 Btu/h | 2.16
Glycol cooled | Ducted | < 29,000 Btu/h | 1.97
|  | ≥ 29,000 Btu/h and < 65,000 Btu/h | 1.93
|  | ≥ 65,000 Btu/h | 1.78
| Nonducted | < 29,000 Btu/h | 2.00
|  | ≥ 29,000 Btu/h and < 65,000 Btu/h | 1.98
|  | ≥ 65,000 Btu/h | 1.81
Glycol cooled with fluid economizer | Ducted | < 29,000 Btu/h | 1.92
|  | ≥ 29,000 Btu/h and < 65,000 Btu/h | 1.88
|  | ≥ 65,000 Btu/h | 1.73
| Nonducted | < 29,000 Btu/h | 1.95
|  | ≥ 29,000 Btu/h and < 65,000 Btu/h | 1.93
|  | ≥ 65,000 Btu/h | 1.76
For SI: 1 British thermal unit per hour = 0.2931 W, oC = [(oF)-32]/1.8, COP = (Btu/h x hp)/(2,550.7).
a | Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure.
b | This table is a replica of ASHRAE 90.1 Table 6.8.1-17 Ceiling-Mounted Computer-Room Air Conditioners —Minimum Efficiency Requirements.

## Table C403.5.1
TABLE C403.5.1
DX COOLING STAGE REQUIREMENTS FOR MODULATING AIRFLOW UNITS
RATING CAPACITY | MINIMUM NUMBER OF MECHANICAL COOLING STAGES | MINIMUM COMPRESSOR DISPLACEMENT a
 65,000 Btu/h and < 240,000 Btu/h | 3 stages |  35% of full load
 240,000 Btu/h | 4 stages |  25% of full load
For SI: 1 British thermal unit per hour = 0.2931 W.
a. For mechanical cooling stage control that does not use variable compressor displacement, the percent displacement shall be equivalent to the mechanical cooling capacity reduction evaluated at the full load rating conditions for the compressor.

## Table C403.7.4.2
TABLE C403.7.4.2
ENERGY RECOVERY REQUIREMENT
(Ventilation systems operating not less than 8,000 hours per year)
PERCENT (%) OUTDOOR AIR AT FULL DESIGN AIRFLOW RATE
 10% and |  20% and |  30% and |  40% and |  50% and |  60% and |  70% and |  80%
< 20% | < 30% | < 40% | < 50% | < 60% | < 70% | < 80%
Design Supply Fan Airflow Rate (cfm)
 2,500 |  2,000 |  1,000 |  500 |  140 |  120 |  100 |  80
For SI: 1 cfm = 0.4719 L/s.

## Table C403.8.1(1)
TABLE C403.8.1(1)
FAN POWER LIMITATION
| LIMIT | CONSTANT VOLUME | VARIABLE VOLUME
Option 1: Fan system motor nameplate hp | Allowable nameplate motor hp | hp  CFMS  0.0011 | hp  CFMS  0.0015
Option 2: Fan system bhp | Allowable fan system bhp | bhp  CFMS  0.00094 + A | bhp  CFMS  0.0013 + A
For SI: 1 bhp = 735.5 W, 1 hp = 745.5 W, 1 cfm = 0.4719 L/s.
where:
CFMS = The maximum design supply airflow rate to conditioned spaces served by the system in cubic feet per minute.
hp = The maximum combined motor nameplate horsepower.
bhp = The maximum combined fan brake horsepower.
A = Sum of [PD  CFMD / 4131].
where:
PD = Each applicable pressure drop adjustment from Table C403.8.1(2) in. w.c.
CFMD = The design airflow through each applicable device from Table C403.8.1(2) in cubic feet per minute.

## Table C403.12.4
TABLE C403.12.4
MINIMUM PIPE INSULATION THICKNESS (in inches)a, c
FLUID OPERATING TEMPERATURE RANGE AND USAGE (F) |  | INSULATION CONDUCTIVITY |  | NOMINAL PIPE OR TUBE SIZE (inches)
|  | Conductivity Btu • in./(h • ft2 • F)b | Mean Rating Temperature, F |  1 | 1 to  11/2 | 11/2 to  4 | 4 to  8 |  8
| 350 | 0.32 – 0.34 | 250 | 4.5 | 5.0 | 5.0 | 5.0 | 5.0
251 – 350 |  | 0.29 – 0.32 | 200 | 3.0 | 4.0 | 4.5 | 4.5 | 4.5
201 – 250 |  | 0.27 – 0.30 | 150 | 2.5 | 2.5 | 2.5 | 3.0 | 3.0
141 – 200 |  | 0.25 – 0.29 | 125 | 1.5 | 1.5 | 2.0 | 2.0 | 2.0
105 – 140 |  | 0.21 – 0.28 | 100 | 1.0 | 1.0 | 1.5 | 1.5 | 1.5
40 – 60 |  | 0.21 – 0.27 | 75 | 0.5 | 0.5 | 1.0 | 1.0 | 1.0
< 40 |  | 0.20 – 0.26 | 50 | 0.5 | 1.0 | 1.0 | 1.0 | 1.5
For SI: 1 inch = 25.4 mm, °C = [(°F) - 32]/1.8.
a | For piping smaller than 11/2 inches and located in partitions within conditioned spaces, reduction of these thicknesses by 1 inch shall be permitted (before thickness adjustment required in footnote b) but not to a thickness less than 1 inch.
b | For insulation outside the stated conductivity range, the minimum thickness (T) shall be determined as follows:
T = r [(1 + t/r)K/k – 1] where:
T = minimum insulation thickness,
r = actual outside radius of pipe,
t = insulation thickness listed in the table for applicable fluid temperature and pipe size,
K = conductivity of alternate material at mean rating temperature indicated for the applicable fluid temperature (Btu • in/h • ft2 • °F) and
k = the upper value of the conductivity range listed in the table for the applicable fluid temperature.
c | For direct-buried heating and hot water system piping, reduction of these thicknesses by 11/2 inches (38 mm) shall be permitted (before thickness adjustment required in footnote b but not to thicknesses less than 1 inch.

## Table C404.10
TABLE C404.10
DEMAND RESPONSIVE CONTROLS FOR WATER HEATING
EQUIPMENT TYPE | CONTROLS
| BEFORE 7/1/2025 a | AFTER 7/1/2025 a
Electric storage water heaters | ANSI/CTA-2045-B Level 1 and also capable of initiating water heating to meet the temperature set point in response to a demand response signal. | ANSI/CTA-2045-B Level 2, except "Price Stream Communication" functionality as defined in the standard.

## Table C405.7
TABLE C405.7
MINIMUM NOMINAL EFFICIENCY LEVELS FOR 10 CFR 431 LOW-VOLTAGE DRY-TYPE DISTRIBUTION TRANSFORMERS
SINGLE-PHASE TRANSFORMERS |  | THREE-PHASE TRANSFORMERS
kVA a | Efficiency (%)b | kVA a | Efficiency (%) b
15 | 97.70 | 15 | 97.89
25 | 98.00 | 30 | 98.23
37.5 | 98.20 | 45 | 98.40
50 | 98.30 | 75 | 98.60
75 | 98.50 | 112.5 | 98.74
100 | 98.60 | 150 | 98.83
167 | 98.70 | 225 | 98.94
250 | 98.80 | 300 | 99.02
333 | 98.90 | 500 | 99.14
— | — | 750 | 99.23
— | — | 1000 | 99.28
a | kiloVolt-Amp rating.
b | Nominal efficiencies shall be established in accordance with the DOE 10 CFR 431 test procedure for low-voltage dry-type transformers.

## Table C405.18
TABLE C405.18
MINIMUM RESERVED AMPERAGE PER SQUARE FOOT OF PLANNED SOLAR AREA
INVERTER SYSTEM VOLTAGE | AMPERAGE PER SQUARE FOOT
120 | 0.125
240 | 0.063
208 | 0.042
277 | 0.054
480 | 0.018